## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Firstlight Network Limited
| Disclosure Date | 2025-08-31
| Disclosure Year (year ended) | 2025-03-31
Template for Schedule 10a
Prepared 16 February 2024.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Firstlight Network Limited
[15 empty] | For Year Ended | 2025-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9
10 |  | 7774 | 1400 Wharerata Road | Gisborne | Muriwai 0905 | 2024-04-01 08:48 | 45383.3667 | 2024-04-01 10:00 | 45383.4167 | 0.0027647 | 3.8398e-05 | 1 | 72 | Unplanned | Wildlife | Replace HV fuse
11 |  | N/A 9 | Tuai | Wairoa | Tuai Sub | 2024-04-02 11:16 | 45384.4694 | 2024-04-02 12:07 | 45384.5049 | 0.0019583 | 3.8398e-05 | 1 | 51 | Unplanned | Human Error | Whilst switching for Transpower shutdowns on the 8th Lost comms, got Genesis to switch manual (Neil)
12 |  | N/A 9 | Tuai | Wairoa | Lake | 2024-04-02 11:16 | 45384.4694 | 2024-04-02 12:07 | 45384.5049 | 0.019583 | 0.00038398 | 10 | 510 | Unplanned | Human Error | Whilst switching for Transpower shutdowns on the 8th Lost comms, got Genesis to switch manual (Neil)
13 |  | N/A 9 | Tuai | Wairoa | Village 2002 | 2024-04-02 11:16 | 45384.4694 | 2024-04-02 12:07 | 45384.5049 | 0.34858 | 0.0068349 | 178 | 9078 | Unplanned | Human Error | Whilst switching for Transpower shutdowns on the 8th Lost comms, got Genesis to switch manual (Neil)
14 |  | N/A 9 | Tuai | Wairoa | Ruakituri 2003 | 2024-04-02 11:16 | 45384.4694 | 2024-04-02 12:07 | 45384.5049 | 0.31724 | 0.0062205 | 162 | 8262 | Unplanned | Human Error | Whilst switching for Transpower shutdowns on the 8th Lost comms, got Genesis to switch manual (Neil)
15 |  | 28690 | Matawai / Te Karaka | Gisborne | Hexton-Puha 50 | 2024-04-03 07:43 | 45385.3215 | 2024-04-03 08:36 | 45385.3583 | 1.2614 | 0.038091 | 992 | 32850 | Unplanned | Defective Equipment | Broken dead end (rust) Dropped conductor
16 |  | 3942 | Tauwhaparae Rd Tutamoe Rd | Gisborne | Tauwhareparae 0404 | 2024-04-03 08:33 | 45385.3562 | 2024-04-03 13:50 | 45385.5764 | 0.48689 | 0.0015359 | 40 | 6351.0586 | Planned | Planned | Replace Poles
17 |  | 3946 | Mahurangi Tiniroto Rd | Wairoa | Ruakituri 2003 | 2024-04-03 09:04 | 45385.3778 | 2024-04-03 15:11 | 45385.6326 | 0.14092 | 0.00038398 | 10 | 1835.7046 | Planned | Planned | Replace Poles
18 |  | 3944 | Tauwhaparae Rd Tutamoe Rd | Gisborne | Tauwhareparae 0404 | 2024-04-05 08:31 | 45387.3549 | 2024-04-05 14:11 | 45387.591 | 0.52221 | 0.0015359 | 40 | 6811.0586 | Planned | Planned | Replace 11kV Poles
19 |  | 6297 | 7078 Waiapu road | Gisborne | Makarika 0204 | 2024-04-06 08:31 | 45388.3549 | 2024-04-06 09:35 | 45388.3993 | 0.0024575 | 3.8398e-05 | 1 | 64 | Unplanned | Unknown cause | Replace HV fuse
20 |  | 6657 | 836 Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2024-04-08 08:28 | 45390.3528 | 2024-04-08 10:00 | 45390.4167 | 0.0070652 | 7.6796e-05 | 2 | 184 | Unplanned | Unknown cause | Replace TX fuse
21 |  | 7501 | 138 Rakankaka Road | Gisborne | Te Arai 0906 | 2024-04-08 19:10 | 45390.7986 | 2024-04-08 20:30 | 45390.8542 | 0.021503 | 0.00026879 | 7 | 560 | Unplanned | Unknown cause | Replace HV fuse
22 |  | 3951 | Morere Hill | Wairoa | Nuhaka 3203 | 2024-04-09 09:00 | 45391.375 | 2024-04-09 14:59 | 45391.6243 | 0.13785 | 0.00038398 | 10 | 1795.6892 | Planned | Planned | Replace Poles
23 |  | 3945 | Matawai Rd Te Wera Rd Koranga Valley Rd Moanui Rd Tahora Rd | Gisborne | Matawai 1204 | 2024-04-09 09:32 | 45391.3972 | 2024-04-09 14:23 | 45391.5993 | 0.8486 | 0.0029183 | 76 | 11085.9181 | Planned | Planned | Pole Replacement
24 |  | 6985 | 646 Tiniroto Road | Gisborne | Lavenham 0902 | 2024-04-10 07:37 | 45392.3174 | 2024-04-10 09:00 | 45392.375 | 0.0095611 | 0.00011519 | 3 | 249 | Unplanned | Wildlife | Replace HV fuse
25 |  | 3896A | Waimata Valley Rd Mander Rd Riverside Rd | Gisborne | Waimata 0903 | 2024-04-10 09:00 | 45392.375 | 2024-04-10 15:48 | 45392.6583 | 0.50132 | 0.0012287 | 32 | 13056 | Planned | Planned | Tree removal works
26 |  | 6984 | 264 Ruakaka Road | Gisborne | Tiniroto 1003 | 2024-04-10 17:53 | 45392.7451 | 2024-04-11 11:00 | 45393.4583 | 0.07887 | 7.6796e-05 | 2 | 2054 | Unplanned | Wildlife | Replace HV fuse - Tiriroto road closed had to go long way round why attended day after
27 |  | 6658 | 846 Kopuapounamu Road | Gisborne | Awatere 0101 | 2024-04-11 07:50 | 45393.3264 | 2024-04-11 12:45 | 45393.5312 | 0.18124 | 0.00061437 | 16 | 4720 | Unplanned | Defective Equipment | Repair broken conductor J2148-J2149 & replace HV fuse links J330
28 |  | 3948 | Matawai | Gisborne | Matawai 1204 | 2024-04-11 08:30 | 45393.3542 | 2024-04-11 14:33 | 45393.6062 | 1.0449 | 0.0028799 | 75 | 13641.7425 | Planned | Planned | Replace Poles
29 |  | 3950 | Makaretu Rd Main Rd Te Karaka Fitzgerald Rd | Gisborne | Matawai 1204 | 2024-04-11 08:48 | 45393.3667 | 2024-04-11 16:38 | 45393.6931 | 0.79407 | 0.0016895 | 44 | 9520.0571 | Planned | Planned | Tree cutting
30 |  | 28761 | Kopuapounamu Road | Gisborne | Awatere 0101 | 2024-04-11 11:00 | 45393.4583 | 2024-04-11 12:20 | 45393.5139 | 0.049149 | 0.00061437 | 16 | 1280 | Unplanned | Defective Equipment | Conductor rusted through
31 |  | 8012 | 395 Spooners Road | Wairoa | Raupunga 3101 | 2024-04-12 09:00 | 45394.375 | 2024-04-12 13:00 | 45394.5417 | 0.027647 | 0.00011519 | 3 | 720 | Unplanned | Unknown cause | Replace Pole & TX fuse
32 |  | 3959 | Tereparataki Waihi Rd | Wairoa | Frasertown 3103 | 2024-04-12 11:08 | 45394.4639 | 2024-04-12 12:55 | 45394.5382 | 0.032869 | 0.00030718 | 8 | 428.1315 | Planned | Planned | Replace Insulators
33 |  | 6983 | E77 Ngakorara Road | Gisborne | Waimata 0903 | 2024-04-12 14:05 | 45394.5868 | 2024-04-12 15:11 | 45394.6326 | 0.060822 | 0.00092155 | 24 | 1584 | Unplanned | Vegetation | Tree on line - removed branch replace HV fuses
34 |  | N/A 7 | Ngakaroa Road | Gisborne | Waimata 0903 | 2024-04-12 14:05 | 45394.5868 | 2024-04-12 15:07 | 45394.6299 | 0.062666 | 0.0013823 | 36 | 1632 | Unplanned | Vegetation | Fire dept report branch on lines on fire. Isolated, removed with hot stick
35 |  | 28763 | Walsh Street | Gisborne | Gladstone 0607 | 2024-04-14 08:30 | 45396.3542 | 2024-04-15 17:20 | 45397.7222 | 0.21726 | 0.0035326 | 92 | 5658 | Unplanned | Defective Equipment | Cable failure up pole B425 at crutch joint
36 |  | 3956 | Matawai Rd Pitcher Rd Te Karaka Poynter Rd | Gisborne | Te Karaka 1203 | 2024-04-14 09:01 | 45396.3757 | 2024-04-14 10:29 | 45396.4368 | 0.15206 | 0.0017279 | 45 | 1984.6654 | Planned | Planned | Install and Connect TX E1529
37 |  | 5776 | Opotoma Road, Nuhaka | Wairoa | Mahia 3301 | 2024-04-14 17:10 | 45396.7153 | 2024-04-14 18:30 | 45396.7708 | 0.046078 | 0.00057597 | 15 | 1200 | Unplanned | Defective Equipment | Replace DDO fuses
38 |  | 3952 | Matawai Rd Te Wera Rd Koranga Valley Rd Moanui Rd Tahora Rd | Gisborne | Matawai 1204 | 2024-04-16 08:32 | 45398.3556 | 2024-04-16 15:37 | 45398.6507 | 1.0771 | 0.0025343 | 66 | 14060.5431 | Planned | Planned | Replace Poles
39 |  | 3952A | Matawai Rd Motu Rd Kerei St Raumati St Neill Rd | Gisborne | Matawai 1204 | 2024-04-16 08:34 | 45398.3569 | 2024-04-16 11:30 | 45398.4792 | 0.23653 | 0.0013439 | 35 | 3084.1393 | Planned | Planned | Replace Poles
40 |  | 3949 | Matawai Rd Te Wera Rd Koranga Valley Rd Moanui Rd Tahora Rd | Gisborne | Matawai 1204 | 2024-04-18 08:30 | 45400.3542 | 2024-04-18 15:15 | 45400.6354 | 0.93445 | 0.0027647 | 72 | 12196.4898 | Planned | Planned | Replace 11kV poles
41 |  | 7778 | 4008 Te Araroa Rd | Gisborne | Awatere 0101 | 2024-04-19 08:03 | 45401.3354 | 2024-04-19 08:38 | 45401.3597 | 0.0013439 | 3.8398e-05 | 1 | 35 | Unplanned | Unknown cause | Replace TX fuse
42 |  | 3953 | Matawai Rd Te Wera Rd Koranga Valley Rd Moanui Rd Tahora Rd | Gisborne | Matawai 1204 | 2024-04-19 08:33 | 45401.3562 | 2024-04-19 13:12 | 45401.55 | 0.6444 | 0.0027647 | 72 | 8416.3796 | Planned | Planned | Replace 11kV Poles
43 |  | N/A 8 | SH 2 Whakaki | Wairoa | Nuhaka 3203 | 2024-04-19 22:35 | 45401.941 | 2024-04-20 00:09 | 45402.0062 | 0.33433 | 0.0047998 | 125 | 8707 | Unplanned | Unknown cause | 2 fuses down @ W8167. Patrolled beyond. Nothing identified. Reloaded fuses and relivened
44 |  | 7502 | 6339 Matawai Road | Gisborne | Matawai 1204 | 2024-04-20 13:33 | 45402.5646 | 2024-04-20 15:30 | 45402.6458 | 0.026955 | 0.00023039 | 6 | 702 | Unplanned | Unknown cause | Replace TX fuse
45 |  | 28777 | Waikura | Gisborne | Hicks Bay 0102 | 2024-04-21 07:19 | 45403.3049 | 2024-04-24 17:30 | 45406.7292 | 0.56802 | 0.00011519 | 3 | 14793 | Unplanned | Lightning | Lightning strike blew TX plus 3 jumpers. Access limited (river in flood)
46 |  | 28701 | Walker Road | Gisborne | Ruatoria 0201 | 2024-04-21 08:00 | 45403.3333 | 2024-04-21 10:47 | 45403.4493 | 0.089775 | 0.00053757 | 14 | 2338 | Unplanned | Defective Equipment | Replaced 11kV x-arm at TX Pole J122
47 |  | 8403 | 1743 Waikura Road | Gisborne | Hicks Bay 0102 | 2024-04-21 17:49 | 45403.7424 | 2024-04-21 20:00 | 45403.8333 | 0.025151 | 0.00019199 | 5 | 655 | Unplanned | Lightning | Replace TX fuse
48 |  | 84041 | 558 Te Kumi Road | Gisborne | Hicks Bay 0102 | 2024-04-21 20:32 | 45403.8556 | 2024-04-21 22:00 | 45403.9167 | 0.010137 | 0.00011519 | 3 | 264 | Unplanned | Unknown cause | Replace HV fuse
49 |  | 7503 | 96 Baillie Road, Waimata | Gisborne | Waimata 0903 | 2024-04-21 20:46 | 45403.8653 | 2024-04-21 22:30 | 45403.9375 | 0.0039934 | 3.8398e-05 | 1 | 104 | Unplanned | Unknown cause | Replace HV fuse
50 |  | 3960 | Ormond Valley Road | Gisborne | Waimata 0903 | 2024-04-22 09:03 | 45404.3771 | 2024-04-22 16:22 | 45404.6819 | 0.57313 | 0.0013055 | 34 | 7098.2549 | Planned | Planned | Tree Clearing for Eastland Treecare
51 |  | 3969 | Whakarau Rd | Gisborne | Matawai 1204 | 2024-04-22 09:04 | 45404.3778 | 2024-04-22 16:03 | 45404.6687 | 0.17698 | 0.00042238 | 11 | 2288.9664 | Planned | Planned | Replace Poles
52 |  | 3966 | Waihi Road | Wairoa | Frasertown 3103 | 2024-04-22 09:45 | 45404.4062 | 2024-04-22 16:06 | 45404.6708 | 0.27796 | 0.00072956 | 19 | 3565.0991 | Planned | Planned | Replace Poles
53 |  | 3971 | Rockhill Rd Tiniroto Rd | Gisborne | W O Kuri 1001 | 2024-04-22 10:56 | 45404.4556 | 2024-04-22 13:44 | 45404.5722 | 0.012902 | 7.6796e-05 | 2 | 168.0129 | Planned | Planned | Install Line markers
54 |  | 5778 | 67 Rotoparu Road | Wairoa | Frasertown 3103 | 2024-04-22 12:25 | 45404.5174 | 2024-04-22 12:36 | 45404.525 | 0.0025343 | 0.00023039 | 6 | 66 | Unplanned | Unknown cause | Replace HV fuse
55 |  | 28688 | Riverpoint Road | Gisborne | Bell 1406 | 2024-04-22 15:53 | 45404.6618 | 2024-04-22 17:01 | 45404.709 | 0.10444 | 0.0015359 | 40 | 2720 | Unplanned | Defective Equipment | Broken x-arm @TX C205 Replaced. Crossarm identified when responding to an LV contact by excavator - 11kV was not a result of LV contact
56 |  | 28775 | Maromaaku Road | Wairoa | Frasertown 3103 | 2024-04-22 20:37 | 45404.859 | 2024-04-23 10:40 | 45405.4444 | 0.16185 | 0.00019199 | 5 | 4215 | Unplanned | Adverse Weather | Repair conductor 2 wires down. Windy raining
57 |  | 3975 | Hicks Bay Te Araroa Rd Waikura | Gisborne | Hicks Bay 0102 | 2024-04-23 08:31 | 45405.3549 | 2024-04-23 16:57 | 45405.7063 | 3.8245 | 0.0086396 | 225 | 47504.6153 | Planned | Planned | Replace 11kV Poles
58 |  | 3965 | Mangone Valley Rd Wai Station Rd | Wairoa | Morere 3401 | 2024-04-23 09:05 | 45405.3785 | 2024-04-23 12:58 | 45405.5403 | 0.66206 | 0.0028415 | 74 | 8652.5401 | Planned | Planned | Relocate Pole W8043
59 |  | 28776 | SH2 Iwtea | Wairoa | Nuhaka 3203 | 2024-04-23 13:49 | 45405.5757 | 2024-04-23 14:18 | 45405.5958 | 0.016703 | 0.00057597 | 15 | 435 | Unplanned | Defective Equipment | Replaced broken binder at Pole
60 |  | 3955 | Riverside Road | Gisborne | Whangara 0506 | 2024-04-24 08:43 | 45406.3632 | 2024-04-24 14:34 | 45406.6069 | 0.17406 | 0.00049917 | 13 | 4533 | Planned | Planned | Replace Poles
61 |  | 3957 | Waiapu Rd SH 35 Kopuaroa Rd Kiekie Rd | Gisborne | Makarika 0204 | 2024-04-24 09:02 | 45406.3764 | 2024-04-24 14:41 | 45406.6118 | 0.19998 | 0.00061437 | 16 | 2604.6629 | Planned | Planned | Replace poles
62 |  | 3970 | Whakarau Rd | Gisborne | Matawai 1204 | 2024-04-24 09:03 | 45406.3771 | 2024-04-24 15:54 | 45406.6625 | 0.1736 | 0.00042238 | 11 | 2261.4548 | Planned | Planned | Replace Poles
63 |  | 3974 | Mahurangi Rd Tiniroto Rd | Wairoa | Ruakituri 2003 | 2024-04-24 09:05 | 45406.3785 | 2024-04-24 14:20 | 45406.5972 | 0.12095 | 0.00038398 | 10 | 1575.6048 | Planned | Planned | Replace Poles
64 |  | 28779 | Waimata Valley Road | Gisborne | Waimata 0903 | 2024-04-24 20:09 | 45406.8396 | 2024-04-25 11:40 | 45407.4861 | 0.21449 | 0.00023039 | 6 | 5586 | Unplanned | Wildlife | Repairs to broken conductor between Poles G539 - G538. Conductor broke mid-span. Potential for turkey strike - Pole condition (blue tag) 11kV x-arm deteriorated badly.
65 |  | 5780 | Kaiwaitau Road, Mahia | Wairoa | Mahia 3301 | 2024-04-25 07:47 | 45407.3243 | 2024-04-25 08:35 | 45407.3576 | 0.064509 | 0.0013439 | 35 | 1680 | Unplanned | Unknown cause | Replace HV fuses
66 |  | 28801 | Aberdeen Rd / Albert St - MVA | Gisborne | Campion 0802 | 2024-04-26 00:21 | 45408.0146 | 2024-04-26 13:29 | 45408.5618 | 3.8671 | 0.031026 | 808 | 100712 | Unplanned | Third Party Interference | Car V's Pole B4038 - Install 300kVA Generator @ TX B440
67 |  | 3977 | Whakarau Road | Gisborne | Matawai 1204 | 2024-04-26 09:03 | 45408.3771 | 2024-04-26 15:30 | 45408.6458 | 0.16346 | 0.00042238 | 11 | 2129.399 | Planned | Planned | Replace Poles
68 |  | 28780 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2024-04-26 09:25 | 45408.3924 | 2024-04-26 14:00 | 45408.5833 | 0.6328 | 0.0032638 | 85 | 16480 | Unplanned | Wildlife | Duck flew into line, clashed and burnt down. Sample brought back 7/16 Cu installed 1954 conductor 600D could see splatter marks
69 |  | 28781 | 660 Mahia Coast Road | Wairoa | Mahia 3301 | 2024-04-26 12:21 | 45408.5146 | 2024-04-27 12:45 | 45409.5312 | 3.8387 | 0.0096763 | 252 | 99971 | Unplanned | Third Party Interference | Person at 660 Felled tree thru line W160-W7626. W160 red tagged, sent bucket from Gisborne. Couldn't fix that night, fixed next day
70 |  | N/A 6 | Tuai Substation | Wairoa | Tuai Sub | 2024-04-29 06:36 | 45411.275 | 2024-04-29 10:09 | 45411.4229 | 0.0081788 | 3.8398e-05 | 1 | 213 | Unplanned | Defective Equipment | Due to faults @ Wairoa T2 (CB112) - Opened 110kV CB172 - Intertripped 110kV CB 302 (Tuai) - Lost comms @ Tuai. Wentia (ex Napier) restored switching & supplied returned.
71 |  | N/A 6 | Tuai Substation | Wairoa | Lake | 2024-04-29 06:36 | 45411.275 | 2024-04-29 10:09 | 45411.4229 | 0.081788 | 0.00038398 | 10 | 2130 | Unplanned | Defective Equipment | Due to faults @ Wairoa T2 (CB112) - Opened 110kV CB172 - Intertripped 110kV CB 302 (Tuai) - Lost comms @ Tuai. Wentia (ex Napier) restored switching & supplied returned.
72 |  | N/A 6 | Tuai Substation | Wairoa | Village 2002 | 2024-04-29 06:36 | 45411.275 | 2024-04-29 10:09 | 45411.4229 | 1.4558 | 0.0068349 | 178 | 37914 | Unplanned | Defective Equipment | Due to faults @ Wairoa T2 (CB112) - Opened 110kV CB172 - Intertripped 110kV CB 302 (Tuai) - Lost comms @ Tuai. Wentia (ex Napier) restored switching & supplied returned.
73 |  | N/A 6 | Tuai Substation | Wairoa | Ruakituri 2003 | 2024-04-29 06:36 | 45411.275 | 2024-04-29 10:09 | 45411.4229 | 1.325 | 0.0062205 | 162 | 34506 | Unplanned | Defective Equipment | Due to faults @ Wairoa T2 (CB112) - Opened 110kV CB172 - Intertripped 110kV CB 302 (Tuai) - Lost comms @ Tuai. Wentia (ex Napier) restored switching & supplied returned.
74 |  | 8501 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2024-04-29 08:23 | 45411.3493 | 2024-04-29 10:00 | 45411.4167 | 0.026072 | 0.00026879 | 7 | 679 | Unplanned | Wildlife | Replaced HV fuses
75 |  | 3972 | Whakarau Rd | Gisborne | Matawai 1204 | 2024-04-29 09:05 | 45411.3785 | 2024-04-29 15:13 | 45411.634 | 0.15544 | 0.00042238 | 11 | 2024.8549 | Planned | Planned | Replace Poles, install HV fuses F2298
76 |  | 3967 | Wheatstone Road | Gisborne | Dalton 0502 | 2024-04-29 09:24 | 45411.3917 | 2024-04-29 11:31 | 45411.4799 | 0.029259 | 0.00023039 | 6 | 762 | Planned | Planned | Upgrade TX A1702P
77 |  | 3973 | Waiapu Rd SH35 Tokomaru Bay | Gisborne | Mata 0304 | 2024-04-29 09:37 | 45411.4007 | 2024-04-29 15:19 | 45411.6382 | 0.052529 | 0.00015359 | 4 | 684.1051 | Planned | Planned | Relocate Pole away from slip
78 |  | 3981 | Nuhaka Opoutama Rd | Wairoa | Mahia 3301 | 2024-04-29 10:00 | 45411.4167 | 2024-04-29 14:42 | 45411.6125 | 0.032485 | 0.00011519 | 3 | 180.0207 | Planned | Planned | Replace 33kV fuse base
79 |  | 5777 | 3 Raukituri Valley | Wairoa | Ruakituri 2003 | 2024-04-29 20:00 | 45411.8333 | 2024-04-29 21:00 | 45411.875 | 0.023039 | 0.00038398 | 10 | 600 | Unplanned | Unknown cause | Replace TX fuses
80 |  | 3968 | Arakihi Rd | Gisborne | Tauwhareparae 0404 | 2024-04-30 08:35 | 45412.3576 | 2024-04-30 14:02 | 45412.5847 | 0.025112 | 7.6796e-05 | 2 | 302.0232 | Planned | Planned | Replace Poles
81 |  | 3978 | Matawai Rd | Gisborne | Matawai 1204 | 2024-04-30 08:56 | 45412.3722 | 2024-04-30 13:04 | 45412.5444 | 0.047614 | 0.00019199 | 5 | 620.1728 | Planned | Planned | Replace Poles
82 |  | 3976 | Utting Rd | Gisborne | Waimata 0903 | 2024-04-30 09:05 | 45412.3785 | 2024-04-30 14:54 | 45412.6208 | 0.17421 | 0.00049917 | 13 | 2269.6324 | Planned | Planned | Tree Clearing
83 |  | N/A2 | Tiniroto Road, Wairoa | Wairoa | Frasertown 3103 | 2024-05-01 14:01 | 45413.584 | 2024-05-01 18:34 | 45413.7736 | 0.41266 | 0.0052221 | 136 | 10747 | Unplanned | Wildlife | B&C phase wrapped at Pole W6494 - W6495. No wind. Suspect bird strike. Line next to river. (untangle with hot stick) Access difficult
84 |  | 28811 | Manuka - Totara St | Gisborne | Elgin 0703 | 2024-05-01 22:08 | 45413.9222 | 2024-05-02 15:15 | 45414.6354 | 2.1243 | 0.093 | 2422 | 55324 | Unplanned | Defective Equipment | Fault in cable crutch
85 |  | 3979 | Tauwhareparae Rd | Gisborne | Tauwhareparae 0404 | 2024-05-02 08:32 | 45414.3556 | 2024-05-02 14:21 | 45414.5979 | 0.37523 | 0.0010751 | 28 | 4891.4187 | Planned | Planned | Replace Poles
86 |  | 7780 | Kora Rd, Tikitiki | Gisborne | Tiki Tiki 0206 | 2024-05-02 12:33 | 45414.5229 | 2024-05-02 13:25 | 45414.559 | 0.013977 | 0.00026879 | 7 | 364 | Unplanned | Unknown cause | Replace HV fuse
87 |  | 8503 | Ngakaroa Road | Gisborne | Waimata 0903 | 2024-05-02 15:44 | 45414.6556 | 2024-05-02 16:30 | 45414.6875 | 0.0088315 | 0.00019199 | 5 | 230 | Unplanned | Wildlife | Replaced fuses DDO
88 |  | 3980 | Te Aroara Rd Te Hue Rd Haig Rd | Gisborne | Awatere 0101 | 2024-05-03 10:01 | 45415.4174 | 2024-05-03 13:49 | 45415.5757 | 0.15759 | 0.00069116 | 18 | 2053.4183 | Planned | Planned | Replace TX J214
89 |  | 8504 | Brown Beach Road | Gisborne | Muriwai 0905 | 2024-05-03 18:07 | 45415.7549 | 2024-05-03 19:55 | 45415.8299 | 0.024882 | 0.00023039 | 6 | 648 | Unplanned | Wildlife | Replaced DDO fuses
90 |  | 28796 | Kanakanaia | Gisborne | Kanakanaia 1202 | 2024-05-04 11:38 | 45416.4847 | 2024-05-04 14:16 | 45416.5944 | 0.60235 | 0.0068732 | 179 | 15687 | Unplanned | Wildlife | Broken conductor at pole E593 after bird strike
91 |  | 5670 | Papatu Rd | Gisborne | Te Arai 0906 | 2024-05-05 09:25 | 45417.3924 | 2024-05-05 10:13 | 45417.4257 | 0.060822 | 0.0012671 | 33 | 1584 | Unplanned | Unknown cause | Replace HV fuse
92 |  | 3984 | Matokitoki Valley Rd Cave Rd | Gisborne | Whangara 0506 | 2024-05-06 11:00 | 45418.4583 | 2024-05-06 12:26 | 45418.5181 | 0.13539 | 0.0015743 | 41 | 1765.7755 | Planned | Planned | Install new TX B1831
93 |  | 3989 | Haisman Rd Hansen Rd Nelson Rd Newstead Rd | Gisborne | Haisman 0804 | 2024-05-06 15:00 | 45418.625 | 2024-05-06 16:00 | 45418.6667 | 0.18178 | 0.0030718 | 80 | 2372.16 | Planned | Planned | Replace 50kV / 11kV poles at Makaraka
94 |  | 3989 | Makaraka | Gisborne | Haisman 0804 | 2024-05-06 15:25 | 45418.6424 | 2024-05-06 15:57 | 45418.6646 | 0.08724 | 0.0027263 | 71 | 2272 | Unplanned | Defective Equipment | Low oil level in RMU C712
95 |  | 1553 | Bell Road | Gisborne | Bell 1406 | 2024-05-06 16:33 | 45418.6896 | 2024-05-06 16:57 | 45418.7063 | 0.0046078 | 0.00019199 | 5 | 120 | Unplanned | Defective Equipment | Low voltage on TX C5157. Tap change carried out
96 |  | 3985 | Tiniroto Rd Main Highway Gisborne | Gisborne | W O Kuri 1001 | 2024-05-07 08:31 | 45419.3549 | 2024-05-07 15:54 | 45419.6625 | 0.23814 | 0.00053757 | 14 | 3102.667 | Planned | Planned | Replace 11kV poles
97 |  | 8317 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2024-05-07 16:00 | 45419.6667 | 2024-05-07 18:00 | 45419.75 | 0.0046078 | 3.8398e-05 | 1 | 120 | Unplanned | Wildlife | Replace HV fuse
98 |  | 8316 | Wharerata Road | Gisborne | Bell 1406 | 2024-05-07 17:13 | 45419.7174 | 2024-05-08 14:00 | 45420.5833 | 0.19153 | 0.00015359 | 4 | 4988 | Unplanned | Wildlife | Birds nest on LV Bushings Replace TX fuse
99 |  | 28828 | Bell Road | Gisborne | Bell 1406 | 2024-05-08 08:28 | 45420.3528 | 2024-05-08 09:29 | 45420.3951 | 0.011711 | 0.00019199 | 5 | 305 | Unplanned | Defective Equipment | Replaced TX C5157
100 |  | 3958A | Taumata Rd | Gisborne | Tahora 1103 | 2024-05-08 09:00 | 45420.375 | 2024-05-08 13:15 | 45420.5521 | 0.21349 | 0.00084476 | 22 | 2781.5325 | Planned | Planned | Replace poles
101 |  | 28797 | 3833 Lake Road | Wairoa | Frasertown 3103 | 2024-05-08 09:40 | 45420.4028 | 2024-05-08 11:12 | 45420.4667 | 0.024728 | 0.00026879 | 7 | 644 | Unplanned | Defective Equipment | Replace TX W1686 - Move HV fuses from W1686 to W4493
102 |  | 3986 | Tiniroto Rd Main Highway Gisborne | Gisborne | W O Kuri 1001 | 2024-05-09 08:32 | 45421.3556 | 2024-05-09 15:55 | 45421.6632 | 0.23814 | 0.00053757 | 14 | 3102.667 | Planned | Planned | Replace Poles
103 |  | 3990 | Valley Rd | Gisborne | Haisman 0804 | 2024-05-09 09:03 | 45421.3771 | 2024-05-09 09:57 | 45421.4146 | 0.029029 | 0.00053757 | 14 | 378.2032 | Planned | Planned | Upgrade TX B3127 to 50kVA
104 |  | N/A1 | Brickworks | Wairoa | Brickworks 3201 | 2024-05-09 12:07 | 45421.5049 | 2024-05-09 14:08 | 45421.5889 | 2.2512 | 0.02373 | 618 | 58629 | Unplanned | Unknown cause | Weather - Wet/Windy. Patrol unable to identify potential cause
105 |  | 3991 | Kaiti Substn - Tyndall Rd, Halley St, Herchell Rd | Gisborne | Herschell 0501 | 2024-05-09 13:00 | 45421.5417 | 2024-05-09 13:26 | 45421.5597 | 0.11681 | 0.0044926 | 117 | 1639.2669 | Planned | Planned | AUFLS protection upgrade
106 |  | 8319 | Grant Rd | Gisborne | Harris 1502 | 2024-05-10 01:19 | 45422.0549 | 2024-05-10 03:00 | 45422.125 | 0.22494 | 0.0022271 | 58 | 5858 | Unplanned | Defective Equipment | Replaced DDO - TX needs replacement
107 |  | 28838 | Mata Rd - Fernside spur | Gisborne | Mata 0304 | 2024-05-10 05:19 | 45422.2215 | 2024-05-13 16:08 | 45425.6722 | 0.34777 | 0.0024575 | 64 | 9057 | Unplanned | Defective Equipment | Broken Pole H4439
108 |  | 3987 | Tiniroto Road | Gisborne | W O Kuri 1001 | 2024-05-10 08:37 | 45422.359 | 2024-05-10 14:30 | 45422.6042 | 0.054218 | 0.00015359 | 4 | 706.1084 | Planned | Planned | Replace Poles
109 |  | 3989B | Haisman Rd Hansen Rd Nelson Rd Newstead Rd | Gisborne | Haisman 0804 | 2024-05-10 09:01 | 45422.3757 | 2024-05-10 09:57 | 45422.4146 | 0.15904 | 0.0030718 | 80 | 2075.6055 | Planned | Planned | Restoration of 11kV & 50kV poles at Makaraka
110 |  | 8322 | Browns Beach Road | Gisborne | Muriwai 0905 | 2024-05-11 18:18 | 45423.7625 | 2024-05-11 19:30 | 45423.8125 | 0.016588 | 0.00023039 | 6 | 432 | Unplanned | Wildlife | Replace HV fuse
111 |  | 8323 | Waihua Road | Gisborne | Rototahi 0403 | 2024-05-12 14:56 | 45424.6222 | 2024-05-12 17:00 | 45424.7083 | 0.014284 | 0.00011519 | 3 | 372 | Unplanned | Wildlife | Replace HV fuse
112 |  | 8015 | Kaiwaitau Road, Mahia | Wairoa | Mahia 3301 | 2024-05-12 17:00 | 45424.7083 | 2024-05-12 18:00 | 45424.75 | 0.080636 | 0.0013439 | 35 | 2100 | Unplanned | Wildlife | Replace HV fuses
113 |  | 3982 | Whakarau Road | Gisborne | Matawai 1204 | 2024-05-13 09:07 | 45425.3799 | 2024-05-13 15:28 | 45425.6444 | 0.029259 | 7.6796e-05 | 2 | 381.0293 | Planned | Planned | Replace Poles
114 |  | 8406 | 82 Jabson Rd | Gisborne | Te Arai 0906 | 2024-05-13 13:09 | 45425.5479 | 2024-05-13 15:00 | 45425.625 | 0.012787 | 0.00011519 | 3 | 333 | Unplanned | Wildlife | Replace Isolation C2172 & TX fuses
115 |  | 28851 | CBD | Gisborne | City 0602 | 2024-05-14 00:54 | 45426.0375 | 2024-05-15 19:16 | 45427.8028 | 0.38433 | 0.0051069 | 133 | 10009 | Unplanned | Defective Equipment | Cable Crutch at RMU B460
116 |  | 3988 | Tiniroto Road | Gisborne | W O Kuri 1001 | 2024-05-14 08:35 | 45426.3576 | 2024-05-14 15:27 | 45426.6438 | 0.22148 | 0.00053757 | 14 | 2885.5504 | Planned | Planned | Replace Poles
117 |  | 3999 | Cricklewood Road | Wairoa | Raupunga 3101 | 2024-05-14 09:05 | 45426.3785 | 2024-05-14 12:09 | 45426.5062 | 0.042391 | 0.00023039 | 6 | 552.2073 | Planned | Planned | Replace poles
118 |  | 3983 | Whakarau Rd Pukekiwi Rd | Gisborne | Matawai 1204 | 2024-05-14 09:06 | 45426.3792 | 2024-05-14 16:19 | 45426.6799 | 0.033253 | 7.6796e-05 | 2 | 414.0318 | Planned | Planned | Replace Poles
119 |  | 28859 | Waima Street | Gisborne | Seaside 0302 | 2024-05-15 10:45 | 45427.4479 | 2024-05-15 11:56 | 45427.4972 | 0.19902 | 0.0028031 | 73 | 5183 | Unplanned | Vegetation | Trees in contact to 11kV OH lines
120 |  | 8410 | Jabson Rd | Gisborne | Te Arai 0906 | 2024-05-15 11:34 | 45427.4819 | 2024-05-15 13:30 | 45427.5625 | 0.013363 | 0.00011519 | 3 | 348 | Unplanned | Wildlife | Replace Isolation C2172 & TX fuses
121 |  | 5787 | 8 Otoi Road | Wairoa | Raupunga 3101 | 2024-05-15 17:52 | 45427.7444 | 2024-05-15 23:30 | 45427.9792 | 0.025957 | 7.6796e-05 | 2 | 676 | Unplanned | Unknown cause | Replace TX fuse
122 |  | 5786 | 2280 Ruapapa Road | Wairoa | Raupunga 3101 | 2024-05-15 18:15 | 45427.7604 | 2024-05-16 14:00 | 45428.5833 | 0.045502 | 3.8398e-05 | 1 | 1185 | Unplanned | Defective Equipment | Replaced HV fuses and replaced TX 16/5/24
123 |  | 5785 | 1151 SH2 Wairoa | Wairoa | Raupunga 3101 | 2024-05-15 18:36 | 45427.775 | 2024-05-15 19:30 | 45427.8125 | 0.0020735 | 3.8398e-05 | 1 | 54 | Unplanned | Lightning | Replaced HV fuses
124 |  | 5784 | Ngamotu Road | Wairoa | Affco 3202 | 2024-05-15 18:55 | 45427.7882 | 2024-05-15 20:00 | 45427.8333 | 0.0049917 | 7.6796e-05 | 2 | 130 | Unplanned | Lightning | Replace TX fuse
125 |  | 5789 | 160A Tawhara Road | Wairoa | Borough One 3204 | 2024-05-16 07:29 | 45428.3118 | 2024-05-16 08:30 | 45428.3542 | 0.0070268 | 0.00011519 | 3 | 183 | Unplanned | Lightning | Replace HV fuses
126 |  | 5792 | 546 Waireka Road | Wairoa | Raupunga 3101 | 2024-05-16 07:40 | 45428.3194 | 2024-05-16 13:30 | 45428.5625 | 0.013439 | 3.8398e-05 | 1 | 350 | Unplanned | Unknown cause | Replace HV fuses
127 |  | 5791 | 202 Otoi Road | Wairoa | Raupunga 3101 | 2024-05-16 08:25 | 45428.3507 | 2024-05-16 12:30 | 45428.5208 | 0.0094075 | 3.8398e-05 | 1 | 245 | Unplanned | Unknown cause | Replace TX fuses
128 |  | 3992 | Tiniroto Rd Main Highway | Gisborne | W O Kuri 1001 | 2024-05-16 08:38 | 45428.3597 | 2024-05-16 16:12 | 45428.675 | 0.24406 | 0.00053757 | 14 | 3095.6632 | Planned | Planned | Replace Poles
129 |  | N/A3 | Whatatutu Rd | Gisborne | Whatatutu 1201 | 2024-05-16 10:11 | 45428.4243 | 2024-05-16 11:16 | 45428.4694 | 0.50474 | 0.0093691 | 244 | 13145 | Unplanned | Unknown cause | Line patrolled from substation to E863. No identifable fault. Pole E1928 - Insulator damaged, potential source.
130 |  | 28863 | Otoi Road | Wairoa | Frasertown 3103 | 2024-05-16 10:39 | 45428.4437 | 2024-05-16 14:59 | 45428.6243 | 0.1198 | 0.00046078 | 12 | 3120 | Unplanned | Lightning | Transformer W446 damaged by Lightnight. Pole W446 red tagged and replaced
131 |  | 8411 | 396 Stafford Rd, Pehiri | Gisborne | Tahunga 1004 | 2024-05-16 11:50 | 45428.4931 | 2024-05-16 15:00 | 45428.625 | 0.021887 | 0.00011519 | 3 | 570 | Unplanned | Unknown cause | Replace DDO fuse @ isolation pole
132 |  | 5790 | 5 Otoi Road | Wairoa | Raupunga 3101 | 2024-05-16 13:04 | 45428.5444 | 2024-05-16 14:10 | 45428.5903 | 0.0050685 | 7.6796e-05 | 2 | 132 | Unplanned | Lightning | Replace HV fuse
133 |  | 28902 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2024-05-17 00:46 | 45429.0319 | 2024-05-17 10:43 | 45429.4465 | 0.81427 | 0.0032638 | 85 | 21206 | Unplanned | Vegetation | Tree thru line D3290 - D3291
134 |  | 3993 | Tiniroto Rd Main Highway | Gisborne | W O Kuri 1001 | 2024-05-17 08:37 | 45429.359 | 2024-05-17 13:19 | 45429.5549 | 0.1516 | 0.00053757 | 14 | 1975.2418 | Planned | Planned | Replace 11kV Poles
135 |  | 3000 | Wainui Rd Wheatstone Rd | Gisborne | Tamarau 0503 | 2024-05-17 09:03 | 45429.3771 | 2024-05-17 10:14 | 45429.4264 | 0.10905 | 0.0015359 | 40 | 2840 | Planned | Planned | Straighten Pole A2335 & Re-sag line A2335-A2922
136 |  | 28869 | Valley Road | Gisborne | Haisman 0804 | 2024-05-17 12:39 | 45429.5271 | 2024-05-17 16:36 | 45429.6917 | 2.5622 | 0.03978 | 1036 | 66728 | Unplanned | Defective Equipment | Fuse Switch B761 faulted
137 |  | 7782 | Anaura Bay Road, Tolaga Bay | Gisborne | Mata 0304 | 2024-05-17 12:39 | 45429.5271 | 2024-05-17 15:25 | 45429.6424 | 0.019122 | 0.00011519 | 3 | 498 | Unplanned | Unknown cause | Replace HV fuses
138 |  | 8016 | 370 SH2 Wairoa | Wairoa | Nuhaka 3203 | 2024-05-18 18:00 | 45430.75 | 2024-05-18 19:30 | 45430.8125 | 0.010367 | 0.00011519 | 3 | 270 | Unplanned | Wildlife | Replace HV fuse
139 |  | 8413 | 137a Moanui Road, Matawai | Gisborne | Matawai 1204 | 2024-05-19 14:39 | 45431.6104 | 2024-05-19 17:30 | 45431.7292 | 0.085359 | 0.00049917 | 13 | 2223 | Unplanned | Wildlife | Remove possum and replace DDO fuse @ F292
140 |  | 6664 | Thatcher Rd, Ruatoria | Gisborne | Tiki Tiki 0206 | 2024-05-20 01:12 | 45432.05 | 2024-05-20 14:35 | 45432.6076 | 0.030834 | 3.8398e-05 | 1 | 803 | Unplanned | Wildlife | Ducks/Geese in paddocks - Replace HV fuses
141 |  | 3004 | State Highway 2 Haliburton Rd Kakariki Rd | Wairoa | Raupunga 3101 | 2024-05-20 10:00 | 45432.4167 | 2024-05-20 10:08 | 45432.4222 | 0.017202 | 0.0021503 | 56 | 224.4817 | Planned | Planned | Replace Poles - Shutdown Cancelled due to Helicopter was unable to fly. Ground team notified @ 10:07
142 |  | 28872 | Solander Street | Gisborne | Solander 0706 | 2024-05-20 15:16 | 45432.6361 | 2024-05-21 16:52 | 45433.7028 | 0.0072572 | 0.00023039 | 6 | 189 | Unplanned | Defective Equipment | 11kV bushing on B422 cracked. Faultman cleaned bushing. Switch soaked for 80min
143 |  | 5796 | 3 Ruakituri Road | Wairoa | Ruakituri 2003 | 2024-05-20 17:21 | 45432.7229 | 2024-05-20 18:30 | 45432.7708 | 0.026495 | 0.00038398 | 10 | 690 | Unplanned | Unknown cause | Replace HV fuse
144 |  | 6990 | Whatatutu Rd | Gisborne | Whatatutu 1201 | 2024-05-20 17:45 | 45432.7396 | 2024-05-20 18:45 | 45432.7812 | 0.023039 | 0.00038398 | 10 | 600 | Unplanned | Defective Equipment | Burning DDO holder
145 |  | N/A4 | Tapuihikitia Road | Gisborne | Whatatutu 1201 | 2024-05-20 18:40 | 45432.7778 | 2024-05-20 19:35 | 45432.816 | 0.018431 | 0.00038398 | 10 | 480 | Unplanned | Defective Equipment | HV Fuse link at F35 burnt out. Line patrolled no apparent cause. WO generated for replacement of HV Fuses @ F35
146 |  | 7789 | 264 Ruakaka Rd | Gisborne | Tiniroto 1003 | 2024-05-20 18:42 | 45432.7792 | 2024-05-20 21:45 | 45432.9062 | 0.014054 | 7.6796e-05 | 2 | 366 | Unplanned | Wildlife | Replace HV fuses
147 |  | 6665 | Beach Road, Tokomaru Bay | Gisborne | Seaside 0302 | 2024-05-21 06:08 | 45433.2556 | 2024-05-21 17:07 | 45433.7132 | 1.2146 | 0.0018431 | 48 | 31632 | Unplanned | Vegetation | Multiple fuses blew, SD to cut trees - Replaced fuses
148 |  | 3005 | Titarangi Rd Jackson Rd | Wairoa | Frasertown 3103 | 2024-05-21 09:15 | 45433.3854 | 2024-05-21 13:22 | 45433.5569 | 0.15175 | 0.00061437 | 16 | 1977.7694 | Planned | Planned | Replace 11kV poles
149 |  | 28907 | Makarika Road | Gisborne | Makarika 0204 | 2024-05-21 10:33 | 45433.4396 | 2024-05-21 10:53 | 45433.4535 | 0.00076796 | 3.8398e-05 | 1 | 20 | Unplanned | Defective Equipment | 11kV conductor hanging low. Possibly due to pole twisting over time
150 |  | 28908 | 4109 SH35 Whangara | Gisborne | Rototahi 0403 | 2024-05-21 10:43 | 45433.4465 | 2024-05-21 14:33 | 45433.6062 | 0.51204 | 0.008294 | 216 | 13335 | Unplanned | Defective Equipment | 11kV road xing brough down at Pole G2993. Deadend gave out on kidney termination
151 |  | 28909 | Beach Rd, Waima | Gisborne | Seaside 0302 | 2024-05-21 12:19 | 45433.5132 | 2024-05-21 17:06 | 45433.7125 | 0.52897 | 0.0018431 | 48 | 13776 | Unplanned | Vegetation | Trees in 400V tripping HV fuses on TX H80 plus other sites. ATS engaged to clear under shutdown
152 |  | 7787 | 1255 Panikau Road, Whangara | Gisborne | Dalton 0502 | 2024-05-21 15:02 | 45433.6264 | 2024-05-21 15:24 | 45433.6417 | 0.0076028 | 0.00034558 | 9 | 198 | Unplanned | Vegetation | Replace HV fuse
153 |  | 7786 | 770 Tutamoe Road, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2024-05-21 16:14 | 45433.6764 | 2024-05-21 22:38 | 45433.9431 | 0.16219 | 0.00042238 | 11 | 4224 | Unplanned | Vegetation | Replace HV fuses
154 |  | N/A5 | SH2 Nuhaka / Morere | Wairoa | Morere 3401 | 2024-05-21 20:12 | 45433.8417 | 2024-05-22 10:40 | 45434.4444 | 0.87348 | 0.013746 | 358 | 22748 | Unplanned | Unknown cause | Isolated fault between CB W790 & RMU W1457. Fault not found see later switching
155 |  | 6667 | 146 Matanui Road, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2024-05-22 04:30 | 45434.1875 | 2024-05-22 08:15 | 45434.3438 | 0.0086396 | 3.8398e-05 | 1 | 225 | Unplanned | Lightning | Lightning night before - Replaced HV fuses
156 |  | 8601 | Paparatu Road | Gisborne | Te Arai 0906 | 2024-05-22 07:33 | 45434.3146 | 2024-05-22 09:00 | 45434.375 | 0.036747 | 0.00042238 | 11 | 957 | Unplanned | Adverse Weather | Replace fuses
157 |  | 3995 | Waikura Valley Rd Te Kumi Rd | Gisborne | Hicks Bay 0102 | 2024-05-22 08:33 | 45434.3562 | 2024-05-22 16:18 | 45434.6792 | 0.69635 | 0.0014975 | 39 | 18135 | Planned | Planned | Replace 11kV Poles
158 |  | 28910 | Raupunga | Wairoa | Raupunga 3101 | 2024-05-22 10:31 | 45434.4382 | 2024-05-29 12:40 | 45441.5278 | 1.2255 | 0.013862 | 361 | 31915 | Unplanned | Defective Equipment | Faulty TX
159 |  | 5795 | Cnr of Clyde Bank Road | Wairoa | Nuhaka 3203 | 2024-05-22 16:20 | 45434.6806 | 2024-05-22 18:30 | 45434.7708 | 0.054909 | 0.00042238 | 11 | 1430 | Unplanned | Unknown cause | Replace HV fuse
160 |  | 7792 | 76 Whakatere Road, Manutuke | Gisborne | Te Arai 0906 | 2024-05-23 07:02 | 45435.2931 | 2024-05-23 11:43 | 45435.4882 | 0.064739 | 0.00023039 | 6 | 1686 | Unplanned | Defective Equipment | Replace HV fuse
161 |  | 7791 | 17 Arero Road, Tolaga Bay | Gisborne | Mata 0304 | 2024-05-23 08:10 | 45435.3403 | 2024-05-23 09:58 | 45435.4153 | 0.004147 | 3.8398e-05 | 1 | 108 | Unplanned | Lightning | Replace HV fuse
162 |  | 7790 | 599 Arakihi Road, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2024-05-23 17:33 | 45435.7312 | 2024-05-24 08:29 | 45436.3535 | 0.10321 | 0.00011519 | 3 | 2688 | Unplanned | Lightning | Replace HV fuse
163 |  | 5797 | Cnr Omana Rd & SH2 | Wairoa | Morere 3401 | 2024-05-24 07:22 | 45436.3069 | 2024-05-24 08:30 | 45436.3542 | 0.031333 | 0.00046078 | 12 | 816 | Unplanned | Unknown cause | Replace HV fuse
164 |  | 3006 | Titirangi Rd Jackson Rd | Wairoa | Frasertown 3103 | 2024-05-24 08:04 | 45436.3361 | 2024-05-24 15:50 | 45436.6597 | 0.2863 | 0.00061437 | 16 | 3730.2904 | Planned | Planned | Replace Poles
165 |  | 6668 | 157 Matakaoa Road | Gisborne | Hicks Bay 0102 | 2024-05-24 08:10 | 45436.3403 | 2024-05-24 10:45 | 45436.4479 | 0.027455 | 0.00030718 | 8 | 715 | Unplanned | Lightning | Lightning replaced fuses
166 |  | 3997 | Waikura Valley Rd Te Kumi Rd | Gisborne | Hicks Bay 0102 | 2024-05-24 08:32 | 45436.3556 | 2024-05-24 12:31 | 45436.5215 | 0.35791 | 0.0014975 | 39 | 4671.0126 | Planned | Planned | Replace poles
167 |  | 28882 | Solander Street | Gisborne | Solander 0706 | 2024-05-24 08:51 | 45436.3688 | 2024-05-24 16:46 | 45436.6986 | 0.0044926 | 0.00023039 | 6 | 117 | Unplanned | Defective Equipment | Low voltage fault reserfaced from earlier in week. Switchgear replaced, Tracking on Bushings All 3 Fuses NOT Tripping.
168 |  | 7793 | Lake Road, Waituhi | Gisborne | Lavenham 0902 | 2024-05-26 06:59 | 45438.291 | 2024-05-26 08:45 | 45438.3646 | 0.024421 | 0.00023039 | 6 | 636 | Unplanned | Wildlife | Replace HV fuses
169 |  | 7794 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2024-05-26 21:00 | 45438.875 | 2024-05-26 21:40 | 45438.9028 | 0.0092155 | 0.00023039 | 6 | 240 | Unplanned | Wildlife | Replace HV Fuses
170 |  | 6666 | 846 Kopuapounamu Road | Gisborne | Awatere 0101 | 2024-05-27 07:03 | 45439.2937 | 2024-05-27 07:45 | 45439.3229 | 0.025803 | 0.00061437 | 16 | 672 | Unplanned | Wildlife | Replaced HD fuse link
171 |  | 3998 | Whakarau road | Gisborne | Matawai 1204 | 2024-05-27 09:05 | 45439.3785 | 2024-05-27 16:06 | 45439.6708 | 0.17782 | 0.00042238 | 11 | 2283.4641 | Planned | Planned | Replace Poles
172 |  | 7795 | 2798 Ihungia Road | Gisborne | Mata 0304 | 2024-05-28 07:38 | 45440.3181 | 2024-05-28 10:32 | 45440.4389 | 0.066813 | 0.00038398 | 10 | 1740 | Unplanned | Unknown cause | Replace HV fuses
173 |  | 3032 | Utting Rd Waimata Valley Rd | Gisborne | Waimata 0903 | 2024-05-28 08:55 | 45440.3715 | 2024-05-28 12:29 | 45440.5201 | 0.22417 | 0.0011135 | 29 | 5838 | Planned | Planned | Tree Cutting
174 |  | 3008 | Cricklewood Road | Wairoa | Raupunga 3101 | 2024-05-28 09:38 | 45440.4014 | 2024-05-28 13:40 | 45440.5694 | 0.046462 | 0.00019199 | 5 | 605.144 | Planned | Planned | Replace Poles W3938 & W3934
175 |  | 3012 | Kowhai Pl Black St Clyde Rd | Wairoa | Borough One 3204 | 2024-05-28 10:04 | 45440.4194 | 2024-05-28 13:37 | 45440.5674 | 0.33533 | 0.0015743 | 41 | 4373.3743 | Planned | Planned | Replace ring main unit
176 |  | 7505 | 61 Pakowhai Road | Gisborne | Muriwai 0905 | 2024-05-28 14:21 | 45440.5979 | 2024-05-28 18:50 | 45440.7847 | 0.16527 | 0.00061437 | 16 | 4304 | Unplanned | Unknown cause | Replace fuse
177 |  | 7506 | 200 Campbells Road, Ngatapa | Gisborne | Lavenham 0902 | 2024-05-29 07:30 | 45441.3125 | 2024-05-29 08:45 | 45441.3646 | 0.023039 | 0.00030718 | 8 | 600 | Unplanned | Unknown cause | Replaced fuse
178 |  | 3009 | Lavenham Road | Gisborne | Waimata 0903 | 2024-05-29 08:31 | 45441.3549 | 2024-05-29 16:05 | 45441.6701 | 1.3946 | 0.0030718 | 80 | 18215.7847 | Planned | Planned | Replace poles
179 |  | 3001 | Whakarau Rd | Gisborne | Matawai 1204 | 2024-05-29 09:01 | 45441.3757 | 2024-05-29 16:07 | 45441.6715 | 0.17993 | 0.00042238 | 11 | 2305.4734 | Planned | Planned | Replace poles
180 |  | 7507 | 69 Saleyards Road | Gisborne | Bell 1406 | 2024-05-29 10:40 | 45441.4444 | 2024-05-29 11:30 | 45441.4792 | 0.021119 | 0.00042238 | 11 | 550 | Unplanned | Unknown cause | Replaced TX fuse
181 |  | 7796 | 2780 Waiapu Road | Gisborne | Mata 0304 | 2024-05-30 07:46 | 45442.3236 | 2024-05-30 09:38 | 45442.4014 | 0.021503 | 0.00019199 | 5 | 560 | Unplanned | Unknown cause | Replace HV fuse
182 |  | 3010 | Lavenham Rd Lake Rd Renner Rd Judd Rd | Gisborne | Lavenham 0902 | 2024-05-30 08:35 | 45442.3576 | 2024-05-30 15:09 | 45442.6312 | 0.84721 | 0.0021503 | 56 | 11055.722 | Planned | Planned | Replace 11kV Poles
183 |  | 3013 | Mclean St Lahore St Sydney St Black St | Wairoa | Borough Two 3205 | 2024-05-30 09:01 | 45442.3757 | 2024-05-30 16:37 | 45442.6924 | 0.928 | 0.0020351 | 53 | 11922.7146 | Planned | Planned | Replace GMTX W1570
184 |  | 7509 | 1180 Arahini Road, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2024-05-30 14:48 | 45442.6167 | 2024-05-30 21:00 | 45442.875 | 0.028568 | 7.6796e-05 | 2 | 744 | Unplanned | Unknown cause | Replace fuses
185 |  | 28918 | Awapuni Road | Gisborne | Willows 0702 | 2024-05-30 15:11 | 45442.6326 | 2024-05-30 15:56 | 45442.6639 | 0.012095 | 0.00026879 | 7 | 315 | Unplanned | Defective Equipment | To replace broken dead-ends on pole B6313
186 |  | 28893 | Lake Road | Gisborne | Lavenham 0902 | 2024-05-30 15:18 | 45442.6375 | 2024-05-30 16:04 | 45442.6694 | 0.098913 | 0.0021503 | 56 | 2576 | Unplanned | Defective Equipment | Post insulator on ABS D322 failed during operation and broke off. Repairs made to ensure ABS D322 closed until permanent reapirs made.
187 |  | 3002 | Whakarau Rd | Gisborne | Matawai 1204 | 2024-05-31 09:03 | 45443.3771 | 2024-05-31 15:04 | 45443.6278 | 0.15248 | 0.00042238 | 11 | 1986.3386 | Planned | Planned | Replace Poles
188 |  | 3020 | Cricklewood Road | Wairoa | Raupunga 3101 | 2024-05-31 09:06 | 45443.3792 | 2024-05-31 13:57 | 45443.5813 | 0.044695 | 0.00015359 | 4 | 582.0922 | Planned | Planned | Replace Pole W536
189 |  | 28926 | Tiniroto Road | Wairoa | Frasertown 3103 | 2024-05-31 17:19 | 45443.7215 | 2024-06-01 14:16 | 45444.5944 | 1.4202 | 0.0052221 | 136 | 36987 | Unplanned | Wildlife | Bindstrike caused side of aged x-arm to brake off and line down at pole W6476. The softwood pole has aged and needs to be replaced.
190 |  | 28927 | All Patutahi Sub | Gisborne | Lavenham 0902 | 2024-05-31 23:00 | 45443.9583 | 2024-06-01 01:18 | 45444.0542 | 1.5694 | 0.020466 | 533 | 40872 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model
191 |  | 28927 | All Patutahi Sub | Gisborne | Muriwai 0905 | 2024-05-31 23:00 | 45443.9583 | 2024-05-31 23:48 | 45443.9917 | 0.72906 | 0.015858 | 413 | 18987 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model
192 |  | 28927 | All Patutahi Sub | Gisborne | Te Arai 0906 | 2024-05-31 23:00 | 45443.9583 | 2024-05-31 23:51 | 45443.9938 | 0.45824 | 0.0089851 | 234 | 11934 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model
193 |  | 28927 | All Patutahi Sub | Gisborne | Waimata 0903 | 2024-05-31 23:00 | 45443.9583 | 2024-06-01 00:37 | 45444.0257 | 1.9818 | 0.021695 | 565 | 51612 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model
194 |  | 28927 | All Patutahi Sub | Gisborne | Patutahi Sub 09 | 2024-05-31 23:00 | 45443.9583 | 2024-05-31 23:50 | 45443.9931 | 0.0019199 | 3.8398e-05 | 1 | 50 | Unplanned | Defective Equipment | Protection fault - updated relay more sensitive to previous model
195 |  | 7510 | 369 Kirkpatrick Rd | Gisborne | Waimata 0903 | 2024-06-01 08:05 | 45444.3368 | 2024-06-01 09:30 | 45444.3958 | 0.026111 | 0.00030718 | 8 | 680 | Unplanned | Unknown cause | Replaced fuse
196 |  | 7511 | 1012 Waimata Rd | Gisborne | Waimata 0903 | 2024-06-01 15:26 | 45444.6431 | 2024-06-01 21:00 | 45444.875 | 0.02565 | 7.6796e-05 | 2 | 668 | Unplanned | Unknown cause | Replaced TX fuse
197 |  | 28931 | Ruakituri Road, Tiniroto Rd | Wairoa | Ruakituri 2003 | 2024-06-02 11:32 | 45445.4806 | 2024-06-04 17:06 | 45447.7125 | 0.7187 | 0.0039166 | 102 | 18717 | Unplanned | Defective Equipment | Repair/Replace broken pole @ W7509 W7510
198 |  | 8019 | 614 Waihua Valley Rd | Wairoa | Raupunga 3101 | 2024-06-04 09:50 | 45447.4097 | 2024-06-04 10:30 | 45447.4375 | 0.0015359 | 3.8398e-05 | 1 | 40 | Unplanned | Unknown cause | Replace HV fuse
199 |  | 3014 | Hill Rd Balance St Stanford Crescent | Gisborne | Aberdeen 0609 | 2024-06-04 10:01 | 45447.4174 | 2024-06-04 11:08 | 45447.4639 | 0.23669 | 0.0035326 | 92 | 3092.8875 | Planned | Planned | Replace 11kV cable termination & Surge arrestors @ B5014
200 |  | 3019 | Tiniroto Rd Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2024-06-04 10:01 | 45447.4174 | 2024-06-04 16:29 | 45447.6868 | 0.64063 | 0.0016511 | 43 | 7731.2796 | Planned | Planned | Isolate 11kV for tree clearing
201 |  | 8018 | Mangatoto Stn | Wairoa | Morere 3401 | 2024-06-04 13:13 | 45447.5507 | 2024-06-04 14:00 | 45447.5833 | 0.0072188 | 0.00015359 | 4 | 188 | Unplanned | Unknown cause | Replaced HV fuse
202 |  | 3962C | Waiapu Rd | Gisborne | Toko Tie 0401 | 2024-06-05 08:30 | 45448.3542 | 2024-06-05 14:34 | 45448.6069 | 0.041931 | 0.00011519 | 3 | 546.0674 | Planned | Planned | Relocate existing poles for new roadway
203 |  | 3003A | SH 2 Iwitea | Wairoa | Nuhaka 3203 | 2024-06-05 09:08 | 45448.3806 | 2024-06-05 16:20 | 45448.6806 | 0.24882 | 0.00057597 | 15 | 3091.7797 | Planned | Planned | Replace 11kV poles
204 |  | 3022 | Ohuka Rd Ebbett Rd | Wairoa | Ruakituri 2003 | 2024-06-06 08:32 | 45449.3556 | 2024-06-06 15:20 | 45449.6389 | 0.43866 | 0.0010751 | 28 | 5718.1412 | Planned | Planned | Tree Cutting
205 |  | 3044 | Seddon St Park Rd Lavenham Rd Cemetery Rd Onslow Rd Atkins St Bilham St | Gisborne | Lavenham 0902 | 2024-06-06 09:01 | 45449.3757 | 2024-06-06 13:21 | 45449.5563 | 0.55908 | 0.0021503 | 56 | 14560 | Planned | Planned | Replace ABS D338
206 |  | 3963C | Waiapu Road | Gisborne | Mata 0304 | 2024-06-06 09:02 | 45449.3764 | 2024-06-06 10:15 | 45449.4271 | 0.0084092 | 0.00011519 | 3 | 109.5674 | Planned | Planned | Run fibre under power. Problem with fibre drum - Shutdown returned early
207 |  | N/A 10 | Patutahi Road | Gisborne | Lavenham 0902 | 2024-06-06 14:35 | 45449.6076 | 2024-06-06 15:41 | 45449.6535 | 0.41792 | 0.017241 | 449 | 10884 | Unplanned | Defective Equipment | Fault on ABS not closed propably after shutdown
208 |  | 7512 | 57 Pitcher Road, Te Karaka | Gisborne | Te Karaka 1203 | 2024-06-07 06:31 | 45450.2715 | 2024-06-07 08:00 | 45450.3333 | 0.023922 | 0.00026879 | 7 | 623 | Unplanned | Unknown cause | Replaced isolation fuse
209 |  | 3024 | SH 2 Iwetea | Wairoa | Nuhaka 3203 | 2024-06-07 09:04 | 45450.3778 | 2024-06-07 14:35 | 45450.6076 | 0.19065 | 0.00057597 | 15 | 2483.9298 | Planned | Planned | Replace poles
210 |  | 28946 | Waihi Rd | Wairoa | Frasertown 3103 | 2024-06-10 03:46 | 45453.1569 | 2024-06-10 07:55 | 45453.3299 | 0.16404 | 0.00791 | 206 | 4272 | Unplanned | Defective Equipment | Conductor came off the insulator at Pole # W4591
211 |  | 28947 | Port Sub | Gisborne | Crawford 1504 | 2024-06-10 06:12 | 45453.2583 | 2024-06-10 06:37 | 45453.2757 | 0.90907 | 0.036363 | 947 | 23675 | Unplanned | Defective Equipment | Relay failed CB A614 tripped
212 |  | 28947 | Port Sub | Gisborne | Esplanade 1503 | 2024-06-10 06:12 | 45453.2583 | 2024-06-10 07:13 | 45453.3007 | 1.7052 | 0.027954 | 728 | 44408 | Unplanned | Defective Equipment | Relay failed CB A614 tripped
213 |  | 28947 | Port Sub | Gisborne | Port A 1501 | 2024-06-10 06:12 | 45453.2583 | 2024-06-10 06:38 | 45453.2764 | 0.19568 | 0.007526 | 196 | 5096 | Unplanned | Defective Equipment | Relay failed CB A614 tripped
214 |  | 28947 | Port Sub | Gisborne | Harris 1502 | 2024-06-10 06:12 | 45453.2583 | 2024-06-10 06:49 | 45453.284 | 1.2105 | 0.032715 | 852 | 31524 | Unplanned | Defective Equipment | Relay failed CB A614 tripped
215 |  | 28950 | Tuporoa Road | Gisborne | Ruatoria 0201 | 2024-06-10 12:05 | 45453.5035 | 2024-06-11 14:02 | 45454.5847 | 0.28065 | 0.0014975 | 39 | 7309 | Unplanned | Defective Equipment | Replace Pole J1629. Repair broken conductor
216 |  | N/A 11 | Tolaga Bay Sub | Gisborne | Rototahi 0403 | 2024-06-10 12:06 | 45453.5042 | 2024-06-10 12:18 | 45453.5125 | 0.099528 | 0.008294 | 216 | 2592 | Unplanned | Wildlife | Seagull (bird) came in contact with 50kV conductor
217 |  | N/A 11 | Tolaga Bay Sub | Gisborne | Town 0402 | 2024-06-10 12:06 | 45453.5042 | 2024-06-10 12:19 | 45453.5132 | 0.10233 | 0.0078716 | 205 | 2665 | Unplanned | Wildlife | Seagull (bird) came in contact with 50kV conductor
218 |  | N/A 11 | Tolaga Bay Sub | Gisborne | Toko Tie 0401 | 2024-06-10 12:06 | 45453.5042 | 2024-06-10 12:21 | 45453.5146 | 0.048382 | 0.0032254 | 84 | 1260 | Unplanned | Wildlife | Seagull (bird) came in contact with 50kV conductor
219 |  | N/A 11 | Tolaga Bay Sub | Gisborne | Tauwhareparae 0404 | 2024-06-10 12:06 | 45453.5042 | 2024-06-10 12:23 | 45453.516 | 0.095304 | 0.0056061 | 146 | 2482 | Unplanned | Wildlife | Seagull (bird) came in contact with 50kV conductor
220 |  | 3007 | Browns Beach Rd State Highway 2 | Gisborne | Muriwai 0905 | 2024-06-10 12:35 | 45453.5243 | 2024-06-10 16:39 | 45453.6937 | 0.056215 | 0.00023039 | 6 | 705.1624 | Planned | Planned | Replace TX Pole C394
221 |  | 3041 | Lavenham Road | Gisborne | Lavenham 0902 | 2024-06-11 08:32 | 45454.3556 | 2024-06-11 16:27 | 45454.6854 | 1.0579 | 0.0022271 | 58 | 27550 | Planned | Planned | Replace Poles
222 |  | 3021 | Bloomfield Rd Riverpoint Rd | Gisborne | Bell 1406 | 2024-06-11 09:04 | 45454.3778 | 2024-06-11 14:28 | 45454.6028 | 0.68425 | 0.0021119 | 55 | 8928.817 | Planned | Planned | Change TX & HV fuses @ C198, C207, C490
223 |  | 3040 | State Highway 2 Haliburton Rd | Wairoa | Raupunga 3101 | 2024-06-11 10:00 | 45454.4167 | 2024-06-11 12:05 | 45454.5035 | 0.26879 | 0.0021503 | 56 | 7000 | Planned | Planned | Replace 11kV Poles
224 |  | 3025 | Wharerata Rd | Gisborne | Bell 1406 | 2024-06-12 08:31 | 45455.3549 | 2024-06-12 11:34 | 45455.4819 | 0.1827 | 0.00099835 | 26 | 2329.3232 | Planned | Planned | Replace TX & TX Fuses C542
225 |  | 3056 | Patutahi Rd Onslow Rd Park Rd Seddon St | Gisborne | Lavenham 0902 | 2024-06-12 09:00 | 45455.375 | 2024-06-12 10:33 | 45455.4396 | 0.21729 | 0.0024191 | 63 | 5659 | Planned | Planned | To remove ABS D1493 & jumper through 11kV
226 |  | 3059 | Kirkpatrick Rd Ellmers Rd | Gisborne | Waimata 0903 | 2024-06-12 09:03 | 45455.3771 | 2024-06-12 13:36 | 45455.5667 | 0.083861 | 0.00030718 | 8 | 2184 | Planned | Planned | Relocate Pole D4767
227 |  | 29007 | Kirkpatrick Rd | Gisborne | Waimata 0903 | 2024-06-12 12:40 | 45455.5278 | 2024-06-12 13:36 | 45455.5667 | 0.051607 | 0.00092155 | 24 | 1344 | Unplanned | Defective Equipment | Replace HV D630
228 |  | 3026 | Bloomfield Road | Gisborne | Bell 1406 | 2024-06-12 13:16 | 45455.5528 | 2024-06-12 15:04 | 45455.6278 | 0.062205 | 0.00057597 | 15 | 810.5184 | Planned | Planned | Replace TX & DDO @ C475
229 |  | 29008 | Awatere | Gisborne | Awatere 0101 | 2024-06-12 14:52 | 45455.6194 | 2024-06-12 17:20 | 45455.7222 | 0.022732 | 0.00015359 | 4 | 592 | Unplanned | Adverse Environment | Slip caused pole to move a conductor to sag close to ground
230 |  | 7191 | Lake Road | Gisborne | Lavenham 0902 | 2024-06-12 17:51 | 45455.7438 | 2024-06-12 19:00 | 45455.7917 | 0.015897 | 0.00023039 | 6 | 414 | Unplanned | Wildlife | Replaced DDO's
231 |  | 3042 | Lavenham Road | Gisborne | Lavenham 0902 | 2024-06-13 08:31 | 45456.3549 | 2024-06-13 16:07 | 45456.6715 | 2.1887 | 0.0047998 | 125 | 28636.793 | Planned | Planned | Replace 11kV/400V poles
232 |  | 3036 | Titirangi Rd Jackson Rd | Wairoa | Frasertown 3103 | 2024-06-13 08:59 | 45456.3743 | 2024-06-13 14:00 | 45456.5833 | 0.18492 | 0.00061437 | 16 | 2409.7694 | Planned | Planned | Replace poles
233 |  | 3027 | Tucker Rd Matawai Rd College RD Brown RD | Gisborne | Waimata 0903 | 2024-06-13 09:05 | 45456.3785 | 2024-06-13 11:01 | 45456.459 | 0.25389 | 0.0021887 | 57 | 3313.2358 | Planned | Planned | To replace TX D413 & DDO fuses
234 |  | 3033 | Pehiri Rd Tahora Rd | Gisborne | Tahunga 1004 | 2024-06-13 10:00 | 45456.4167 | 2024-06-13 12:33 | 45456.5229 | 0.088123 | 0.00057597 | 15 | 1148.1609 | Planned | Planned | To replace kidney insulators
235 |  | 3028 | Snowsill Road | Gisborne | Waimata 0903 | 2024-06-13 13:04 | 45456.5444 | 2024-06-13 14:52 | 45456.6194 | 0.045617 | 0.00042238 | 11 | 594.2509 | Planned | Planned | Replace TX E52 & HV Fuses E52
236 |  | 28955 | Grey Street | Gisborne | Port A 1501 | 2024-06-14 03:30 | 45457.1458 | 2024-06-14 06:04 | 45457.2528 | 0.058211 | 0.00061437 | 16 | 1516 | Unplanned | Defective Equipment | Fault in RMU (Fust Switch) B1047
237 |  | 3043 | Lavenham Road | Gisborne | Lavenham 0902 | 2024-06-14 08:31 | 45457.3549 | 2024-06-14 14:13 | 45457.5924 | 0.89406 | 0.0027647 | 72 | 12198.2017 | Unplanned | Human Error | Changing Poles - P # 28923
238 |  | 3060 | Wharekopae Rd Main Rd | Gisborne | Ngatapa 1102 | 2024-06-14 09:01 | 45457.3757 | 2024-06-14 11:32 | 45457.4806 | 0.034789 | 0.00023039 | 6 | 906 | Planned | Planned | Replace pole D4039 - Post car V's pole
239 |  | 3030 | Ormond Valley Rd Whitmore Rd | Gisborne | Waimata 0903 | 2024-06-14 09:05 | 45457.3785 | 2024-06-14 12:11 | 45457.5076 | 0.23569 | 0.0012671 | 33 | 3074.0179 | Planned | Planned | Replace TX Pole E853
240 |  | 3035 | Tiniroto Road | Wairoa | Frasertown 3103 | 2024-06-14 09:05 | 45457.3785 | 2024-06-14 13:36 | 45457.5667 | 0.29136 | 0.0010751 | 28 | 3798.5156 | Planned | Planned | Replace poles
241 |  | 3038 | Waiapu Rd | Gisborne | Mata 0304 | 2024-06-14 09:32 | 45457.3972 | 2024-06-14 13:44 | 45457.5722 | 0.038705 | 0.00015359 | 4 | 504.0922 | Planned | Planned | Excavations below 11kV for battering hill
242 |  | 28956 | Waimata Valley Road | Gisborne | Waimata 0903 | 2024-06-14 18:32 | 45457.7722 | 2024-06-14 22:50 | 45457.9514 | 0.45678 | 0.0032254 | 84 | 11896 | Unplanned | Vegetation | 2 Wires down E1198 - E1199 - Tree thru line
243 |  | 7190 | 1180 Arakihi Road | Gisborne | Tauwhareparae 0404 | 2024-06-15 07:26 | 45458.3097 | 2024-06-15 09:30 | 45458.3958 | 0.0095227 | 7.6796e-05 | 2 | 248 | Unplanned | Adverse Weather | Replaced DDO's
244 |  | 7189 | Bond Road, Ormond | Gisborne | Waimata 0903 | 2024-06-15 20:01 | 45458.834 | 2024-06-15 20:30 | 45458.8542 | 0.022271 | 0.00076796 | 20 | 580 | Unplanned | Wildlife | Replaced DDO's
245 |  | 3037 | Ford Road | Gisborne | Waimata 0903 | 2024-06-17 09:02 | 45460.3764 | 2024-06-17 10:23 | 45460.4326 | 0.037323 | 0.00046078 | 12 | 486.2239 | Planned | Planned | Straighten Pole E2258 - E2259. Resag 11kV & 400V conductors
246 |  | N/A 15 | Te Araroa Road | Gisborne | Awatere 0101 | 2024-06-17 10:00 | 45460.4167 | 2024-06-17 11:43 | 45460.4882 | 0.013977 | 0.010483 | 273 | 364 | Unplanned | Human Error | Wiring fault in AUFLS scheme caused CB to open when testing - CB J523
247 |  | 3048 | Back Ormond Rd Sterling Park Silverstone Pl | Gisborne | Haisman 0804 | 2024-06-17 10:02 | 45460.4181 | 2024-06-17 16:51 | 45460.7021 | 1.5291 | 0.0056445 | 147 | 19939.9662 | Planned | Planned | To connect 11kV cable, dismantle 11kV OH
248 |  | 3029 A | Te Araroa Road | Gisborne | Awatere 0101 | 2024-06-18 09:19 | 45461.3882 | 2024-06-18 15:43 | 45461.6549 | 0.53081 | 0.0013823 | 36 | 6921.5547 | Planned | Planned | Replace Pole J3363
249 |  | 1572 | Arapata Rd | Wairoa | Raupunga 3101 | 2024-06-18 10:19 | 45461.4299 | 2024-06-20 15:27 | 45463.6438 | 1.1351 | 0.016012 | 417 | 29562 | Unplanned | Vegetation | Trees through line @ W5588 where wires are down. Caused jaint failure at span W1719 & broke poles
250 |  | 3023A | Lake Rd Ruapapa Rd Titirangi Rd Rangiahua Rd Cricklewood Rd | Wairoa | Frasertown 3103 | 2024-06-18 11:42 | 45461.4875 | 2024-06-18 15:18 | 45461.6375 | 0.00061437 | 0.00015359 | 4 | 16 | Unplanned | Human Error | Replace hanging arm on pole TX W1647
251 |  | 3023A | Lake Rd Ruapapa Rd Titirangi Rd Rangiahua Rd Cricklewood Rd | Wairoa | Frasertown 3103 | 2024-06-18 11:44 | 45461.4889 | 2024-06-18 15:17 | 45461.6368 | 0.8097 | 0.0038014 | 99 | 10599.9509 | Planned | Planned | Replace hanging arm on TX pole W1647
252 |  | 3046 | Tiniroto Road Main Highway | Gisborne | W O Kuri 1001 | 2024-06-19 08:39 | 45462.3604 | 2024-06-19 15:44 | 45462.6556 | 0.22847 | 0.00053757 | 14 | 2976.5993 | Planned | Planned | Replace 11kV Poles
253 |  | 6992 | 4876 Tiniroto Road | Gisborne | Tiniroto 1003 | 2024-06-19 09:19 | 45462.3882 | 2024-06-19 12:45 | 45462.5312 | 0.00791 | 3.8398e-05 | 1 | 206 | Unplanned | Lightning | Replace DDO's
254 |  | 1574 | Ngatapa | Gisborne | Ngatapa Sub 11 | 2024-06-19 23:12 | 45462.9667 | 2024-06-19 23:36 | 45462.9833 | 0.00092155 | 3.8398e-05 | 1 | 24 | Unplanned | Defective Equipment | H Structure D943 collapsed
255 |  | 1574 | Ngatapa | Gisborne | Totangi 1101 | 2024-06-19 23:12 | 45462.9667 | 2024-06-19 23:36 | 45462.9833 | 0.012902 | 0.00053757 | 14 | 336 | Unplanned | Defective Equipment | H Structure D943 collapsed
256 |  | 1574 | Ngatapa | Gisborne | Ngatapa 1102 | 2024-06-19 23:12 | 45462.9667 | 2024-06-19 23:36 | 45462.9833 | 0.064509 | 0.0026879 | 70 | 1680 | Unplanned | Defective Equipment | H Structure D943 collapsed
257 |  | 1574 | Ngatapa | Gisborne | Tahora 1103 | 2024-06-19 23:12 | 45462.9667 | 2024-06-19 23:36 | 45462.9833 | 0.13915 | 0.0057981 | 151 | 3624 | Unplanned | Defective Equipment | H Structure D943 collapsed
258 |  | 1574 | Ngatapa | Gisborne | W O Kuri 1001 | 2024-06-19 23:12 | 45462.9667 | 2024-06-20 00:50 | 45463.0347 | 0.17686 | 0.0018047 | 47 | 4606 | Unplanned | Defective Equipment | H Structure D943 collapsed
259 |  | 1574 | Ngatapa | Gisborne | Tiniroto 1003 | 2024-06-19 23:12 | 45462.9667 | 2024-06-20 00:52 | 45463.0361 | 0.47998 | 0.0047998 | 125 | 12500 | Unplanned | Defective Equipment | H Structure D943 collapsed
260 |  | 1574 | Ngatapa | Gisborne | Tahunga 1004 | 2024-06-19 23:12 | 45462.9667 | 2024-06-20 00:50 | 45463.0347 | 0.18439 | 0.0018815 | 49 | 4802 | Unplanned | Defective Equipment | H Structure D943 collapsed
261 |  | 1574 | Ngatapa | Gisborne | Parikanapa 1002 | 2024-06-19 23:12 | 45462.9667 | 2024-06-20 00:51 | 45463.0354 | 0.11404 | 0.0011519 | 30 | 2970 | Unplanned | Defective Equipment | H Structure D943 collapsed
262 |  | 1574 | Ngatapa | Gisborne | Pehiri Sub 10 | 2024-06-19 23:12 | 45462.9667 | 2024-06-20 00:50 | 45463.0347 | 0.003763 | 3.8398e-05 | 1 | 98 | Unplanned | Defective Equipment | H Structure D943 collapsed
263 |  | 29027 | Lloyd George Road | Gisborne | Tamarau 0503 | 2024-06-20 09:42 | 45463.4042 | 2024-06-20 10:56 | 45463.4556 | 0.1989 | 0.0026879 | 70 | 5180 | Unplanned | Defective Equipment | Repair broken strands mid span, cause unknown
264 |  | 28967 | Port feeder being fed by Crawford at time of fault | Gisborne | Crawford 1504 | 2024-06-20 10:48 | 45463.45 | 2024-06-20 15:51 | 45463.6604 | 1.8553 | 0.055447 | 1444 | 48318 | Unplanned | Defective Equipment | Jumper blown at ABS A4110 due to AFLS switching. Later found faulty lightening arrestor @ A6458
265 |  | 5672 | 1809 McMillan & Matawai Rd | Gisborne | Te Karaka 1203 | 2024-06-21 07:09 | 45464.2979 | 2024-06-21 09:45 | 45464.4062 | 0.02396 | 0.00015359 | 4 | 624 | Unplanned | Unknown cause | Replace fuses
266 |  | 3049 | Tiniroto Rd Main Highway | Gisborne | Kanakanaia 1202 | 2024-06-21 08:30 | 45464.3542 | 2024-06-21 15:01 | 45464.6257 | 0.85466 | 0.0021887 | 57 | 11141.1824 | Planned | Planned | Replace Poles
267 |  | 3031 | Tyndall Road | Gisborne | Herschell 0501 | 2024-06-21 13:00 | 45464.5417 | 2024-06-21 14:23 | 45464.5993 | 0.56092 | 0.0067581 | 176 | 7353.3608 | Planned | Planned | AUFLS protection testing on CB A473
268 |  | 5673 | 82 Jobson Road | Gisborne | Te Arai 0906 | 2024-06-23 08:00 | 45466.3333 | 2024-06-23 09:30 | 45466.3958 | 0.010367 | 0.00011519 | 3 | 270 | Unplanned | Unknown cause | Fuse fault
269 |  | 29036 | Poroporo Road | Gisborne | Tiki Tiki 0206 | 2024-06-23 17:42 | 45466.7375 | 2024-07-02 16:55 | 45475.7049 | 1.6141 | 0.0032254 | 84 | 42036 | Unplanned | Defective Equipment | Broken conductor from J1004 to J1006. Poles/Conductor replaced. (River in-flood - no access to pole sites). Tree in River broke conductor ? TCL
270 |  | 29034 | 3km South of Nicks Head Stn Road / SH2 | Gisborne | Muriwai 0905 | 2024-06-23 21:46 | 45466.9069 | 2024-06-24 11:53 | 45467.4951 | 1.0827 | 0.0053373 | 139 | 28196 | Unplanned | Third Party Interference | Car V's Pole @ Pole C3561
271 |  | 3051 | Glenroy Road | Gisborne | Dalton 0502 | 2024-06-24 09:09 | 45467.3812 | 2024-06-24 14:17 | 45467.5951 | 0.24836 | 0.00080636 | 21 | 3236.6078 | Planned | Planned | Upgrade TX A222 & TX A435
272 |  | 5573 | 1400 Wharerata Road | Gisborne | Muriwai 0905 | 2024-06-24 14:57 | 45467.6229 | 2024-06-24 15:30 | 45467.6458 | 0.0012671 | 3.8398e-05 | 1 | 33 | Unplanned | Unknown cause | Replace Fuses
273 |  | 3054 | Solander Street | Gisborne | Solander 0706 | 2024-06-24 16:07 | 45467.6715 | 2024-06-24 21:43 | 45467.9049 | 0.012902 | 3.8398e-05 | 1 | 336 | Unplanned | Defective Equipment | Planned - Replace Oil RMU with Gas Switch RMU B1043, B1044, B1045
274 |  | 3052 | Kanakanaia Rd Bruce Rd | Gisborne | Kanakanaia 1202 | 2024-06-25 08:31 | 45468.3549 | 2024-06-25 13:47 | 45468.5743 | 0.68828 | 0.0021887 | 57 | 8973.7314 | Planned | Planned | Replace Poles
275 |  | 3061 | Titirangi Rd Jackson Rd | Wairoa | Frasertown 3103 | 2024-06-25 09:24 | 45468.3917 | 2024-06-25 13:05 | 45468.5451 | 0.13578 | 0.00061437 | 16 | 1769.7694 | Planned | Planned | Replace poles
276 |  | 28982 | 1673 Tiniroto Road | Gisborne | W O Kuri 1001 | 2024-06-25 11:45 | 45468.4896 | 2024-06-25 15:32 | 45468.6472 | 0.034865 | 0.00015359 | 4 | 908 | Unplanned | Defective Equipment | Replaced TX D173
277 |  | 29136 | Mata Road about Tuakau Road | Gisborne | Mata 0304 | 2024-06-25 12:28 | 45468.5194 | 2024-06-27 19:32 | 45470.8139 | 3.806 | 0.0011519 | 30 | 99120 | Unplanned | Vegetation | Tree through 11kV @ Pole H1206 (see fault sheet #9)
278 |  | 28993 | Waihau Bay Road | Gisborne | Rototahi 0403 | 2024-06-25 15:42 | 45468.6542 | 2024-07-04 12:48 | 45477.5333 | 6.5799 | 0.044119 | 1149 | 171360 | Unplanned | Vegetation | Tress through line. Slip across road prevented access to site. Blown jumper, town feeding Rotutahi, Dalton feeding A140
279 |  | N/A 18 | Papuni Road | Wairoa | Ruakituri 2003 | 2024-06-25 15:54 | 45468.6625 | 2024-06-28 13:06 | 45471.5458 | 4.2521 | 0.0081404 | 212 | 110737 | Unplanned | Adverse Weather | o/c trip on W816. Line patrol & Heli patrol did not identify any obvious fault cause
280 |  | 28984 | Waimata | Gisborne | Waimata 0903 | 2024-06-25 16:03 | 45468.6687 | 2024-06-30 16:44 | 45473.6972 | 7.8681 | 0.0080252 | 209 | 204910 | Unplanned | Vegetation | Muitiple faults tree thru line
281 |  | 29119 | Waiapu Road | Gisborne | Mata 0304 | 2024-06-25 17:53 | 45468.7451 | 2024-06-28 17:05 | 45471.7118 | 3.8246 | 0.0032638 | 85 | 99603 | Unplanned | Vegetation | Tree through line @ Pole G703
282 |  | 28992 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2024-06-25 17:55 | 45468.7465 | 2024-06-26 09:27 | 45469.3938 | 1.2439 | 0.0057981 | 151 | 32396 | Unplanned | Vegetation | Tree thru line broke conductor & arm
283 |  | N/A 14 | SH35 Waipiro Road | Gisborne | Inland 0301 | 2024-06-25 18:10 | 45468.7569 | 2024-06-26 14:20 | 45469.5972 | 1.1016 | 0.013823 | 360 | 28690 | Unplanned | Vegetation | Trees across lines between H62 - H2021
284 |  | 29108 | Waipiro Road | Gisborne | Inland 0301 | 2024-06-25 18:10 | 45468.7569 | 2024-07-02 19:29 | 45475.8118 | 2.8426 | 0.0028799 | 75 | 74029 | Unplanned | Vegetation | Trees brought down poles & lines between H2246 & H2209
285 |  | 29102 | Awapuni Road | Gisborne | Lytton 0701 | 2024-06-25 19:11 | 45468.7993 | 2024-06-25 20:25 | 45468.8507 | 0.17417 | 0.0027263 | 71 | 4536 | Unplanned | Vegetation | GDC trees thru line - wet & windy
286 |  | 29043 | Te Araroa & Ruatoria | Gisborne | Ruatoria 0201 | 2024-06-25 19:16 | 45468.8028 | 2024-06-25 19:26 | 45468.8097 | 0.11865 | 0.011865 | 309 | 3090 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached
287 |  | 29043 | Te Araroa & Ruatoria | Gisborne | Tiki Tiki 0206 | 2024-06-25 19:16 | 45468.8028 | 2024-06-26 04:35 | 45469.191 | 1.3187 | 0.012134 | 316 | 34344 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached
288 |  | 29043 | Te Araroa & Ruatoria | Gisborne | Makarika 0204 | 2024-06-25 19:16 | 45468.8028 | 2024-06-27 10:45 | 45470.4479 | 0.32542 | 0.008678 | 226 | 8475 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached
289 |  | 29043 | Te Araroa & Ruatoria | Gisborne | Te Araroa 0103 | 2024-06-25 19:16 | 45468.8028 | 2024-06-26 03:45 | 45469.1562 | 0.47921 | 0.0099835 | 260 | 12480 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached
290 |  | 29043 | Te Araroa & Ruatoria | Gisborne | Hicks Bay 0102 | 2024-06-25 19:16 | 45468.8028 | 2024-06-26 04:11 | 45469.1743 | 1.1548 | 0.01966 | 512 | 30074 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached
291 |  | 29043 | Te Araroa & Ruatoria | Gisborne | Awatere 0101 | 2024-06-25 19:16 | 45468.8028 | 2024-06-26 04:36 | 45469.1917 | 0.50989 | 0.01605 | 418 | 13279 | Unplanned | Vegetation | Tree on 50kV line @ Pole - Photo attached
292 |  | 28988 | Waihua | Wairoa | Raupunga 3101 | 2024-06-25 19:36 | 45468.8167 | 2024-06-26 16:40 | 45469.6944 | 11.8361 | 0.015436 | 402 | 308247 | Unplanned | Vegetation | Tree through lines - See 22, 27
293 |  | 29105 | Tapuaeroa | Gisborne | Tiki Tiki 0206 | 2024-06-25 19:45 | 45468.8229 | 2024-06-26 16:20 | 45469.6806 | 1.7619 | 0.0015359 | 40 | 45884 | Unplanned | Adverse Weather | Wires down - windy
294 |  | 29048 | Nuhaka - Mahia | Wairoa | Morere 3401 | 2024-06-25 20:18 | 45468.8458 | 2024-06-25 21:10 | 45468.8819 | 0.14115 | 0.010291 | 268 | 3676 | Unplanned | Adverse Weather | Multiply faults conductor clashing
295 |  | 29048 | Nuhaka - Mahia | Wairoa | Mahia 3301 | 2024-06-25 20:18 | 45468.8458 | 2024-06-28 13:00 | 45471.5417 | 8.1406 | 0.17698 | 4609 | 212006 | Unplanned | Adverse Weather | Multiply faults conductor clashing
296 |  | 29103 | Matokitoki Valley Road | Gisborne | Whangara 0506 | 2024-06-25 22:56 | 45468.9556 | 2024-06-26 14:48 | 45469.6167 | 4.8338 | 0.044926 | 1170 | 125886 | Unplanned | Defective Equipment | Faulty Lightning Arrestor @ TX B641
297 |  | N/A 12 | Entire Crawford Feeder | Gisborne | Crawford 1504 | 2024-06-26 00:20 | 45469.0139 | 2024-06-26 00:41 | 45469.0285 | 0.76362 | 0.036363 | 947 | 19887 | Unplanned | Defective Equipment | Fault Initally not found. Later found faulty Lightening arrestor @ A6458
298 |  | 29107 | Whatatutu Rd | Gisborne | Whatatutu 1201 | 2024-06-26 00:32 | 45469.0222 | 2024-07-01 15:07 | 45474.6299 | 2.6275 | 0.0051069 | 133 | 68429 | Unplanned | Vegetation | Tree across line between ABS E174 & HV links E739 - E773-E775 E777-E778
299 |  | 29114 | Ruakituri - Crosshills | Wairoa | Ruakituri 2003 | 2024-06-26 00:40 | 45469.0278 | 2024-06-28 17:16 | 45471.7194 | 7.8447 | 0.007142 | 186 | 204300 | Unplanned | Vegetation | Trees through line byd - Cut jumpers @ pole W7327
300 |  | N/A 17 | Kotemaori | Wairoa | Raupunga 3101 | 2024-06-26 04:13 | 45469.1757 | 2024-06-26 14:52 | 45469.6194 | 0.70656 | 0.0069116 | 180 | 18401 | Unplanned | Adverse Weather | Unknown feeding Raupunga - See 12, 27
301 |  | 29101 | Kings Road | Gisborne | Bushmere 0805 | 2024-06-26 04:46 | 45469.1986 | 2024-06-26 11:18 | 45469.4708 | 0.16557 | 0.00042238 | 11 | 4312 | Unplanned | Vegetation | Tree thru lines - high winds
302 |  | 29127 | Wai-O-Moko Road | Gisborne | Dalton 0502 | 2024-06-26 05:27 | 45469.2271 | 2024-06-29 11:38 | 45472.4847 | 2.7604 | 0.0044158 | 115 | 71889 | Unplanned | Adverse Environment | Fallen pole beyond HV links A4017 - in river. Wet & Windy - see 5
303 |  | 29115 | Puha | Gisborne | Puha Sub 12 | 2024-06-26 05:54 | 45469.2458 | 2024-06-26 06:12 | 45469.2583 | 0.00069116 | 3.8398e-05 | 1 | 18 | Unplanned | Defective Equipment | Broken pole stay gave way
304 |  | 29115 | Puha | Gisborne | Whatatutu 1201 | 2024-06-26 05:54 | 45469.2458 | 2024-06-26 06:12 | 45469.2583 | 0.16864 | 0.0093691 | 244 | 4392 | Unplanned | Defective Equipment | Broken pole stay gave way
305 |  | 29115 | Puha | Gisborne | Kanakanaia 1202 | 2024-06-26 05:54 | 45469.2458 | 2024-06-26 06:12 | 45469.2583 | 0.12372 | 0.0068732 | 179 | 3222 | Unplanned | Defective Equipment | Broken pole stay gave way
306 |  | 29115 | Puha | Gisborne | Te Karaka 1203 | 2024-06-26 05:54 | 45469.2458 | 2024-06-26 06:12 | 45469.2583 | 0.12579 | 0.0069884 | 182 | 3276 | Unplanned | Defective Equipment | Broken pole stay gave way
307 |  | 29115 | Puha | Gisborne | Matawai 1204 | 2024-06-26 05:54 | 45469.2458 | 2024-06-26 06:12 | 45469.2583 | 0.2661 | 0.014783 | 385 | 6930 | Unplanned | Defective Equipment | Broken pole stay gave way
308 |  | 29117 | Lake Road | Wairoa | Frasertown 3103 | 2024-06-26 07:47 | 45469.3243 | 2024-06-28 14:09 | 45471.5896 | 7.181 | 0.014054 | 366 | 187016 | Unplanned | Vegetation | Out of zone tree went through line broke 50/11kV Pole - see 12, 22
309 |  | N/A 19 | Wairoa Town | Wairoa | Borough One 3204 | 2024-06-26 08:09 | 45469.3396 | 2024-06-26 11:25 | 45469.4757 | 5.5348 | 0.056867 | 1481 | 144144 | Unplanned | Adverse Weather | a Park switch station under threath of flood waters - Off Loaded
310 |  | 28985 | SH35 Whangara Road | Gisborne | Dalton 0502 | 2024-06-26 09:36 | 45469.4 | 2024-06-26 11:51 | 45469.4938 | 0.73302 | 0.0056829 | 148 | 19090 | Unplanned | Adverse Weather | Broken conductor High winds
311 |  | 28986 | Tansley Road | Gisborne | Lavenham 0902 | 2024-06-26 09:54 | 45469.4125 | 2024-06-26 12:46 | 45469.5319 | 0.066045 | 0.00038398 | 10 | 1720 | Unplanned | Adverse Weather | Broke conductor - high winds
312 |  | 29045 | Mata Road | Gisborne | Mata 0304 | 2024-06-26 10:35 | 45469.441 | 2024-06-27 18:42 | 45470.7792 | 1.2771 | 0.00076796 | 20 | 33260 | Unplanned | Vegetation | High winds blew conductor into trees. Cleared from tree using liveline stick
313 |  | N/A 16 | All feeders | Gisborne | Te Araroa Sub 01 | 2024-06-26 11:06 | 45469.4625 | 2024-06-26 11:37 | 45469.484 | 0.76339 | 0.027339 | 712 | 19881 | Unplanned | Unknown cause | Generator CB1 tripped on O/C
314 |  | 29049 | Wharerata Road | Gisborne | Muriwai 0905 | 2024-06-26 12:49 | 45469.534 | 2024-06-28 17:54 | 45471.7458 | 1.9154 | 0.010214 | 266 | 49884 | Unplanned | Vegetation | Tree cleared from line @ Pole C3768 & C5992 (2 faults). Feeder stayed in for 6 min, tree found on line
315 |  | 29113 | Marumaru | Wairoa | Frasertown 3103 | 2024-06-26 12:52 | 45469.5361 | 2024-06-27 15:23 | 45470.641 | 4.4258 | 0.002995 | 78 | 115261 | Unplanned | Vegetation | Tree through line W6021 - W6022 & W5866 - W5867 - 2 x faults
316 |  | 5571 | Hororoa Rd | Gisborne | Tauwhareparae 0404 | 2024-06-26 13:57 | 45469.5813 | 2024-06-29 16:00 | 45472.6667 | 0.68241 | 0.00015359 | 4 | 17772 | Unplanned | Unknown cause | Fuse fault
317 |  | 29110 | Mangaopono Road | Gisborne | Tiki Tiki 0206 | 2024-06-26 16:30 | 45469.6875 | 2024-06-30 14:57 | 45473.6229 | 0.30081 | 0.00088315 | 23 | 7834 | Unplanned | Vegetation | Tree thru line - Remove tree & repair 11kV conductor
318 |  | 29111 | Lake Road | Wairoa | Frasertown 3103 | 2024-06-26 21:00 | 45469.875 | 2024-06-28 11:36 | 45471.4833 | 2.177 | 0.016818 | 438 | 56695 | Unplanned | Vegetation | Tree through line beyond W4297 & W4300
319 |  | 29106 | Waingake | Gisborne | Te Arai 0906 | 2024-06-26 21:07 | 45469.8799 | 2024-06-27 17:25 | 45470.7257 | 2.6224 | 0.0038398 | 100 | 68296 | Unplanned | Adverse Weather | Broken Conductor high winds C793 - C100
320 |  | 29046 | Tauhara Valley | Wairoa | Brickworks 3201 | 2024-06-27 13:45 | 45470.5729 | 2024-06-27 14:46 | 45470.6153 | 0.0070268 | 0.00011519 | 3 | 183 | Unplanned | Defective Equipment | Open jumper @ TX W1591
321 |  | 29051 | Kopupounama Road | Gisborne | Awatere 0101 | 2024-06-27 16:14 | 45470.6764 | 2024-06-27 18:20 | 45470.7639 | 0.07741 | 0.00061437 | 16 | 2016 | Unplanned | Vegetation | Conductor brought down by tree
322 |  | 6993 | 168 Wharf road | Gisborne | Rototahi 0403 | 2024-06-28 11:59 | 45471.4993 | 2024-06-29 08:00 | 45472.3333 | 0.092232 | 7.6796e-05 | 2 | 2402 | Unplanned | Adverse Weather | Replace fuses
323 |  | 29129 | Berry Road | Gisborne | Tiniroto 1003 | 2024-06-28 13:24 | 45471.5583 | 2024-06-29 15:14 | 45472.6347 | 0.47614 | 0.00030718 | 8 | 12400 | Unplanned | Vegetation | Tree thru line broke pole
324 |  | 28990 | Panikau Road | Gisborne | Dalton 0502 | 2024-06-28 15:17 | 45471.6368 | 2024-06-29 16:08 | 45472.6722 | 0.057251 | 3.8398e-05 | 1 | 1491 | Unplanned | Vegetation | Clear trees and repair conductor
325 |  | 28991 | Tiniroto Road | Gisborne | Lavenham 0902 | 2024-06-29 09:53 | 45472.4118 | 2024-06-29 11:12 | 45472.4667 | 0.091003 | 0.0011519 | 30 | 2370 | Unplanned | Vegetation | Trees damage conductor
326 |  | 29130 | Parikanapa Road | Gisborne | Parikanapa 1002 | 2024-06-29 12:22 | 45472.5153 | 2024-06-29 15:00 | 45472.625 | 0.05921 | 0.00046078 | 12 | 1542 | Unplanned | Defective Equipment | No apparent cause for fault
327 |  | 28994 | Whakapunake line | Wairoa | Ruakituri 2003 | 2024-06-29 15:59 | 45472.666 | 2024-06-30 12:26 | 45473.5181 | 0.047114 | 3.8398e-05 | 1 | 1227 | Unplanned | Defective Equipment | Repair broken jumper
328 |  | 5574 | 1118 Wharerata Road | Gisborne | Muriwai 0905 | 2024-06-30 08:36 | 45473.3583 | 2024-06-30 09:00 | 45473.375 | 0.0055293 | 0.00023039 | 6 | 144 | Unplanned | Unknown cause | Fuse fault
329 |  | 5572 | 187 Berry Road | Gisborne | Tiniroto 1003 | 2024-06-30 09:30 | 45473.3958 | 2024-06-30 11:30 | 45473.4792 | 0.023039 | 0.00019199 | 5 | 600 | Unplanned | Unknown cause | Fuse fault
330 |  | 28996 | Hillside Road | Gisborne | Ngatapa 1102 | 2024-06-30 14:13 | 45473.5924 | 2024-06-30 15:57 | 45473.6646 | 0.0079868 | 7.6796e-05 | 2 | 208 | Unplanned | Defective Equipment | Repair broken conductor
331 |  | 29126 | Arikihi road | Gisborne | Tauwhareparae 0404 | 2024-06-30 15:00 | 45473.625 | 2024-06-30 18:06 | 45473.7542 | 0.014284 | 7.6796e-05 | 2 | 372 | Unplanned | Vegetation | Wires down G1645 - G1643
332 |  | N/A 13 | Feeder fault - Crawford | Gisborne | Crawford 1504 | 2024-06-30 15:24 | 45473.6417 | 2024-06-30 16:10 | 45473.6736 | 1.4317 | 0.036363 | 947 | 37286 | Unplanned | Wildlife | Fault Initally not found. Patrol would indicate potential bird strike
333 |  | 6994 | Goodwin Road | Gisborne | Whangara 0506 | 2024-07-01 08:50 | 45474.3681 | 2024-07-01 13:00 | 45474.5417 | 0.028799 | 0.00011519 | 3 | 750 | Unplanned | Adverse Weather | Replace fuses
334 |  | 29054 | 20km Waimata Valely Road | Gisborne | Waimata 0903 | 2024-07-01 13:44 | 45474.5722 | 2024-07-01 14:39 | 45474.6104 | 0.0042238 | 7.6796e-05 | 2 | 110 | Unplanned | Defective Equipment | Replaced TX G188
335 |  | 29055 | Cave Road | Gisborne | Whangara 0506 | 2024-07-01 14:21 | 45474.5979 | 2024-07-01 14:49 | 45474.6174 | 0.0010751 | 3.8398e-05 | 1 | 28 | Unplanned | Defective Equipment | Broken insulator + conductor down @ Pole A2795
336 |  | 29056 | Waihua Valley Road | Wairoa | Raupunga 3101 | 2024-07-01 14:41 | 45474.6118 | 2024-07-02 16:30 | 45475.6875 | 1.3255 | 0.013708 | 357 | 34521 | Unplanned | Defective Equipment | Pole W3892 failed
337 |  | 3065 | Onepoto Rd Waimoko Rd Lake Rd | Wairoa | Village 2002 | 2024-07-02 10:13 | 45475.4257 | 2024-07-02 14:12 | 45475.5917 | 0.94524 | 0.003955 | 103 | 11736.7359 | Planned | Planned | Tree clearing
338 |  | 6996 | 187 Berry Road | Gisborne | Tiniroto 1003 | 2024-07-02 10:18 | 45475.4292 | 2024-07-02 14:15 | 45475.5938 | 0.1274 | 0.00053757 | 14 | 3318 | Unplanned | Adverse Weather | Replace fuses
339 |  | 6671 | 4934 Waiapu Road | Gisborne | Inland 0301 | 2024-07-02 11:51 | 45475.4938 | 2024-07-03 07:15 | 45476.3021 | 0.044695 | 3.8398e-05 | 1 | 1164 | Unplanned | Unknown cause | Fuse fault
340 |  | 29135 | Marumoko Road | Gisborne | Matawai 1204 | 2024-07-02 13:11 | 45475.5493 | 2024-07-03 12:50 | 45476.5347 | 0.49756 | 0.0036094 | 94 | 12958 | Unplanned | Vegetation | Trees brought down 6 span HV conductor
341 |  | 29058 | Te Araroa | Gisborne | Hicks Bay 0102 | 2024-07-02 13:25 | 45475.559 | 2024-07-02 13:34 | 45475.5653 | 0.088469 | 0.0098299 | 256 | 2304 | Unplanned | Vegetation | Tree fell on 50kV line @ Pole J1877
342 |  | 29058 | Te Araroa | Gisborne | Te Araroa 0103 | 2024-07-02 13:25 | 45475.559 | 2024-07-02 13:35 | 45475.566 | 0.049533 | 0.0049533 | 129 | 1290 | Unplanned | Vegetation | Tree fell on 50kV line @ Pole J1877
343 |  | 29058 | Te Araroa | Gisborne | Awatere 0101 | 2024-07-02 13:25 | 45475.559 | 2024-07-02 13:36 | 45475.5667 | 0.038436 | 0.0034942 | 91 | 1001 | Unplanned | Vegetation | Tree fell on 50kV line @ Pole J1877
344 |  | 29058 | Te Araroa | Gisborne | Te Araroa Sub 01 | 2024-07-02 13:25 | 45475.559 | 2024-07-02 13:33 | 45475.5646 | 0.00030718 | 3.8398e-05 | 1 | 8 | Unplanned | Vegetation | Tree fell on 50kV line @ Pole J1877
345 |  | 6995 | 1400 Wharerata Road | Gisborne | Muriwai 0905 | 2024-07-02 14:06 | 45475.5875 | 2024-07-02 18:00 | 45475.75 | 0.0089851 | 3.8398e-05 | 1 | 234 | Unplanned | Wildlife | Replace fuses
346 |  | 7402 | 187 Berry Road | Gisborne | Tiniroto 1003 | 2024-07-03 19:20 | 45476.8056 | 2024-07-04 09:30 | 45477.3958 | 0.26111 | 0.00030718 | 8 | 6800 | Unplanned | Wildlife | Replaced fuses
347 |  | 6999 | 209 Brown Beach Road | Gisborne | Muriwai 0905 | 2024-07-04 07:26 | 45477.3097 | 2024-07-04 09:00 | 45477.375 | 0.021656 | 0.00023039 | 6 | 564 | Unplanned | Wildlife | Replace fuses
348 |  | 3066 | Anaura Bay Rd Lockwood Rd | Gisborne | Mata 0304 | 2024-07-04 09:00 | 45477.375 | 2024-07-04 16:00 | 45477.6667 | 0.9515 | 0.0022655 | 59 | 12418.0693 | Planned | Planned | Replace 11kV poles
349 |  | N/A 21 | Hokoroa Road, Waimata Valley Road | Gisborne | Waimata 0903 | 2024-07-04 09:19 | 45477.3882 | 2024-07-04 09:35 | 45477.3993 | 0.0036862 | 0.00023039 | 6 | 96 | Unplanned | Human Error | HV Links G527 Open/Close to ensure closed fully
350 |  | 29069 | Crawford Rd & De Latour Rd | Gisborne | Crawford 1504 | 2024-07-04 17:54 | 45477.7458 | 2024-07-04 19:55 | 45477.8299 | 2.63 | 0.036363 | 947 | 68492 | Unplanned | Defective Equipment | Faulty lightening arrestor @ A6458
351 |  | 3074 | Lavenham Road | Gisborne | Lavenham 0902 | 2024-07-05 08:59 | 45478.3743 | 2024-07-05 10:25 | 45478.434 | 0.013209 | 0.00015359 | 4 | 172.0264 | Planned | Planned | Upgrade TX D366
352 |  | 3073 | Maki Street | Gisborne | Esplanade 1503 | 2024-07-05 09:00 | 45478.375 | 2024-07-05 09:27 | 45478.3938 | 0.0020735 | 7.6796e-05 | 2 | 54 | Planned | Planned | Change SW/GR
353 |  | 3072 | Anaura Rd Lockwood Rd | Gisborne | Mata 0304 | 2024-07-05 09:05 | 45478.3785 | 2024-07-05 12:07 | 45478.5049 | 0.062896 | 0.00034558 | 9 | 819.4665 | Planned | Planned | Replace LV Pole
354 |  | 3039 | Erepeti Rd | Wairoa | Ruakituri 2003 | 2024-07-05 09:12 | 45478.3833 | 2024-07-05 13:42 | 45478.5708 | 0.072572 | 0.00026879 | 7 | 945.2822 | Planned | Planned | Cut Trees
355 |  | 29070 | Anaura Bay Road | Gisborne | Mata 0304 | 2024-07-05 09:16 | 45478.3861 | 2024-07-05 11:12 | 45478.4667 | 0.26199 | 0.0022655 | 59 | 6823 | Unplanned | Defective Equipment | Conductor break in binder @ G1471 (part power response)
356 |  | 3075 | Lavenham Road | Gisborne | Lavenham 0902 | 2024-07-05 12:47 | 45478.5326 | 2024-07-05 14:45 | 45478.6146 | 0.004531 | 3.8398e-05 | 1 | 59.0023 | Planned | Planned | Upgrade TX
357 |  | 7404 | 418 Waiatai Valley Rd | Wairoa | Nuhaka 3203 | 2024-07-05 13:02 | 45478.5431 | 2024-07-05 14:00 | 45478.5833 | 0.031179 | 0.00053757 | 14 | 812 | Unplanned | Third Party Interference | Replaced fuses
358 |  | 3073A | Maki Street | Gisborne | Esplanade 1503 | 2024-07-05 16:02 | 45478.6681 | 2024-07-05 16:08 | 45478.6722 | 0.00046078 | 7.6796e-05 | 2 | 12 | Planned | Planned | Change SW/GR
359 |  | 6674 | Puhanga Road | Gisborne | Makarika 0204 | 2024-07-06 07:26 | 45479.3097 | 2024-07-06 10:00 | 45479.4167 | 0.088699 | 0.00057597 | 15 | 2310 | Unplanned | Defective Equipment | conductor badly pitted (clashing?)
360 |  | 3063 | Lavenham Road | Gisborne | Lavenham 0902 | 2024-07-07 09:01 | 45480.3757 | 2024-07-07 10:15 | 45480.4271 | 0.20458 | 0.0027647 | 72 | 2672.9575 | Planned | Planned | Upgrade TX
361 |  | 3067 | Anarua Bay Road | Gisborne | Mata 0304 | 2024-07-08 09:00 | 45481.375 | 2024-07-08 16:16 | 45481.6778 | 0.98775 | 0.0022655 | 59 | 12418.0693 | Planned | Planned | Pole Replacements
362 |  | 3089 | Glenroy Rd Waiomoko Rd Andrews Rd Pa Rd | Gisborne | Dalton 0502 | 2024-07-08 10:03 | 45481.4187 | 2024-07-08 14:20 | 45481.5972 | 0.83842 | 0.0033022 | 86 | 21835 | Planned | Planned | To restore 11kV Conductor
363 |  | 3076 A | Motu Road | Gisborne | Matawai 1204 | 2024-07-09 08:30 | 45482.3542 | 2024-07-09 09:00 | 45482.375 | 0.10613 | 0.0044158 | 115 | 1386.4074 | Planned | Planned | Replace poles & ABS F228
364 |  | 3076 | Motu Road | Gisborne | Matawai 1204 | 2024-07-09 09:00 | 45482.375 | 2024-07-09 16:28 | 45482.6861 | 0.28276 | 0.00065277 | 17 | 3571.1692 | Planned | Planned | Replace poles & ABS F228
365 |  | 3078 | Valley Rd Duncan St Justin St Campbell St | Gisborne | Haisman 0804 | 2024-07-09 09:02 | 45482.3764 | 2024-07-09 15:58 | 45482.6653 | 2.2578 | 0.0056061 | 146 | 29467.441 | Planned | Planned | Replaced RMU (Oil) with RMU (Gas)
366 |  | 3077 | Mohaka Coach Rd | Wairoa | Raupunga 3101 | 2024-07-09 09:08 | 45482.3806 | 2024-07-09 13:10 | 45482.5486 | 0.032523 | 0.00023039 | 6 | 418.5625 | Planned | Planned | Install HV Fuses W5846. Repair 11kV damage
367 |  | 3076 B | Motu Road | Gisborne | Matawai 1204 | 2024-07-09 16:00 | 45482.6667 | 2024-07-09 17:46 | 45482.7403 | 0.30864 | 0.004339 | 113 | 3173.9323 | Planned | Planned | Replace poles & ABS F228
368 |  | 3076 | Motu Road | Gisborne | Matawai 1204 | 2024-07-09 16:36 | 45482.6917 | 2024-07-09 17:46 | 45482.7403 | 0.0026879 | 3.8398e-05 | 1 | 70 | Unplanned | Human Error | Replacing poles & ABS F228
369 |  | N/A 20 | Wairoa Town | Wairoa | Borough Two 3205 | 2024-07-09 17:22 | 45482.7236 | 2024-07-09 19:55 | 45482.8299 | 2.1555 | 0.03882 | 1011 | 56136 | Unplanned | Unknown cause | Cause not found. Report of a bang in Ruthford St
370 |  | 3068 | Anaura Bay Rd Lockwood Rd | Gisborne | Mata 0304 | 2024-07-10 09:00 | 45483.375 | 2024-07-10 15:53 | 45483.6618 | 0.93564 | 0.0022655 | 59 | 12211.1015 | Planned | Planned | Pole replacement
371 |  | 7407 | 412 Waiaka Road | Wairoa | Nuhaka 3203 | 2024-07-10 11:49 | 45483.4924 | 2024-07-10 13:00 | 45483.5417 | 0.038168 | 0.00053757 | 14 | 994 | Unplanned | Unknown cause | Replaced fuses
372 |  | 3071 A | Waiapu road | Gisborne | Seaside 0302 | 2024-07-11 08:32 | 45484.3556 | 2024-07-11 09:02 | 45484.3764 | 0.12902 | 0.0043006 | 112 | 1574.7433 | Planned | Planned | To install new TX H4009. To replace ABSD H246
373 |  | 3071 | Waiapu road | Gisborne | Seaside 0302 | 2024-07-11 09:10 | 45484.3819 | 2024-07-11 13:11 | 45484.5493 | 0.99942 | 0.004147 | 108 | 13081.1812 | Planned | Planned | To install new TX H4009. To replace ABSD H246
374 |  | 3079 | Crawford Rd De Lautour Rutene Rd Shaw St Wainui Rd | Gisborne | Esplanade 1503 | 2024-07-11 09:32 | 45484.3972 | 2024-07-11 16:41 | 45484.6951 | 1.8944 | 0.0044158 | 115 | 22408.5159 | Planned | Planned | Replace TX A345
375 |  | 3071 B | Waiapu road | Gisborne | Seaside 0302 | 2024-07-11 16:01 | 45484.6674 | 2024-07-11 16:27 | 45484.6854 | 0.11182 | 0.0043006 | 112 | 1462.2616 | Planned | Planned | To install new TX H4009. To replace ABSD H246
376 |  | 6679 | 84 Koia Road | Gisborne | Tiki Tiki 0206 | 2024-07-11 18:45 | 45484.7812 | 2024-07-11 19:40 | 45484.8194 | 0.014783 | 0.00026879 | 7 | 385 | Unplanned | Lightning | Bad Lightning
377 |  | 3069 | Anaura Bay Rd Lockwood Rd | Gisborne | Mata 0304 | 2024-07-12 09:00 | 45485.375 | 2024-07-12 14:32 | 45485.6056 | 0.75214 | 0.0022655 | 59 | 9816.1882 | Planned | Planned | Replace HV poles
378 |  | 3070 | Matokitoki Valley Road | Gisborne | Whangara 0506 | 2024-07-12 09:03 | 45485.3771 | 2024-07-12 13:00 | 45485.5417 | 0.00061437 | 7.6796e-05 | 2 | 16 | Unplanned | Human Error | Install ABS B1834. Replace ABS B78 with HV Links B78
379 |  | 3070 | Matokitoki Valley Rd Howarth St Justin St | Gisborne | Whangara 0506 | 2024-07-12 09:03 | 45485.3771 | 2024-07-12 13:02 | 45485.5431 | 0.96106 | 0.0041086 | 107 | 12541.5512 | Planned | Planned | Install ABS B1834. Replace ABS B78 with HV Links B78
380 |  | 29092 | Matawai Road | Gisborne | Matawai 1204 | 2024-07-12 12:47 | 45485.5326 | 2024-07-12 14:33 | 45485.6062 | 0.0040702 | 3.8398e-05 | 1 | 106 | Unplanned | Defective Equipment | Replaced faulty transformer
381 |  | 7409 | 764 Awamate Road | Wairoa | Frasertown 3103 | 2024-07-14 23:44 | 45487.9889 | 2024-07-15 13:00 | 45488.5417 | 0.15282 | 0.00019199 | 5 | 3980 | Unplanned | Unknown cause | Replaced fuses
382 |  | 8414 | 1706 Parikanapa Road | Gisborne | Parikanapa 1002 | 2024-07-15 11:44 | 45488.4889 | 2024-07-15 13:00 | 45488.5417 | 0.0058365 | 7.6796e-05 | 2 | 152 | Unplanned | Unknown cause | Replaced ddo fuses
383 |  | 8415 | 210 Pa Road | Gisborne | Dalton 0502 | 2024-07-16 06:28 | 45489.2694 | 2024-07-16 09:28 | 45489.3944 | 0.19353 | 0.0010751 | 28 | 5040 | Unplanned | Defective Equipment | Replace fuses
384 |  | 29146 | Pa Road, Whangara | Gisborne | Dalton 0502 | 2024-07-16 08:10 | 45489.3403 | 2024-07-16 09:28 | 45489.3944 | 0.083861 | 0.0010751 | 28 | 2184 | Unplanned | Defective Equipment | Repaired broken binder pole A1246
385 |  | 6678 | 84 Koia Road | Gisborne | Tiki Tiki 0206 | 2024-07-16 08:16 | 45489.3444 | 2024-07-16 12:30 | 45489.5208 | 0.068272 | 0.00026879 | 7 | 1778 | Unplanned | Lightning | Lightning overnight
386 |  | 3088 | Matawai & Otoko Areas | Gisborne | Matawai 1204 | 2024-07-16 09:00 | 45489.375 | 2024-07-16 17:37 | 45489.734 | 4.9254 | 0.018124 | 472 | 57626.7278 | Planned | Planned | Pole, Switchgear, TX Replacements
387 |  | 3088a | Matawai & Otoko Areas | Gisborne | Matawai 1204 | 2024-07-16 09:00 | 45489.375 | 2024-07-16 10:15 | 45489.4271 | 0.087356 | 0.0026879 | 70 | 525.7056 | Planned | Planned | Pole, Switchgear, TX Replacements
388 |  | 3088b | Matawai & Otoko Areas | Gisborne | Matawai 1204 | 2024-07-16 17:09 | 45489.7146 | 2024-07-16 17:33 | 45489.7312 | 0.032254 | 0.0013439 | 35 | 0 | Planned | Planned | Pole, Switchgear, TX Replacements
389 |  | 3096 | Whatatutu Rd Mangamaia Rd Armstrong Rd Tarndale Rd | Gisborne | Whatatutu 1201 | 2024-07-17 09:33 | 45490.3979 | 2024-07-17 13:55 | 45490.5799 | 1.8572 | 0.0071036 | 185 | 48366 | Planned | Planned | Replace ABS F362
390 |  | 8417 | 542 Waitangi Road | Gisborne | Kanakanaia 1202 | 2024-07-18 07:45 | 45491.3229 | 2024-07-18 09:00 | 45491.375 | 0.037438 | 0.00049917 | 13 | 975 | Unplanned | Unknown cause | Replace ddo fuses
391 |  | 3087 | Caesar Road | Gisborne | Waimata 0903 | 2024-07-18 08:07 | 45491.3382 | 2024-07-18 08:23 | 45491.3493 | 0.0036862 | 0.00023039 | 6 | 48.0111 | Planned | Planned | Shelterbelt Trimming
392 |  | 3086 | Brown Road | Gisborne | Waimata 0903 | 2024-07-18 09:02 | 45491.3764 | 2024-07-18 10:05 | 45491.4201 | 0.036286 | 0.00057597 | 15 | 435.2505 | Planned | Planned | Shelterbelt Trimming
393 |  | 3083 | Waiomoko Rd Andrews Rd | Gisborne | Dalton 0502 | 2024-07-18 09:03 | 45491.3771 | 2024-07-18 15:44 | 45491.6556 | 0.32335 | 0.00080636 | 21 | 4213.8952 | Planned | Planned | Replace Poles
394 |  | 3090 | Muriwai Beach Road | Gisborne | Muriwai 0905 | 2024-07-18 09:04 | 45491.3778 | 2024-07-18 13:40 | 45491.5694 | 0.64647 | 0.0023423 | 61 | 8437.7173 | Planned | Planned | Install TX C4704
395 |  | 29151 | Frasertown Road | Wairoa | Nuhaka 3203 | 2024-07-18 12:03 | 45491.5021 | 2024-07-18 14:32 | 45491.6056 | 0.32039 | 0.0021503 | 56 | 8344 | Unplanned | Third Party Interference | Car versus pole W6681
396 |  | 3111 | De Latour Rd Seymour Rd Martin Rd Turenne St Owen St Kelvin St Vivian St Huxley St Tui St Kara St | Gisborne | Crawford 1504 | 2024-07-19 09:01 | 45492.3757 | 2024-07-19 10:43 | 45492.4465 | 1.0222 | 0.010022 | 261 | 26622 | Planned | Planned | To remove faulty LA and Rejoin 11kV jumpers
397 |  | 29210 | Ngatapa | Gisborne | Ngatapa Sub 11 | 2024-07-20 18:57 | 45493.7896 | 2024-07-20 21:58 | 45493.9153 | 1.1723 | 0.033598 | 875 | 30529 | Unplanned | Unknown cause | High fault current on Totangi (2k+ amps) cause trip on D13 (incomer) & 50kV CB D31. During initial restoration switching the circuilativy current in VR resulted in tripping CB D640 (Lavenham)
398 |  | 9301 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2024-07-22 07:59 | 45495.3326 | 2024-07-22 09:23 | 45495.391 | 0.019353 | 0.00023039 | 6 | 504 | Unplanned | Wildlife | Replaced fuses
399 |  | 7798 | 1473 Waikura Road | Gisborne | Hicks Bay 0102 | 2024-07-22 08:32 | 45495.3556 | 2024-07-22 13:29 | 45495.5618 | 0.057021 | 0.00019199 | 5 | 1485 | Unplanned | Unknown cause | Replaced fuse
400 |  | 3084 | Waiomoko Rd Andrews Rd | Gisborne | Dalton 0502 | 2024-07-22 09:03 | 45495.3771 | 2024-07-22 14:15 | 45495.5938 | 0.25158 | 0.00080636 | 21 | 3278.6416 | Planned | Planned | Replace Poles
401 |  | 9302 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2024-07-22 10:30 | 45495.4375 | 2024-07-22 11:15 | 45495.4688 | 0.010367 | 0.00023039 | 6 | 270 | Unplanned | Wildlife | Replaced fuses
402 |  | 9303 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2024-07-22 17:33 | 45495.7312 | 2024-07-22 18:16 | 45495.7611 | 0.0099067 | 0.00023039 | 6 | 258 | Unplanned | Wildlife | Replaced fuses
403 |  | 7410 | 764 Awamate Road | Wairoa | Frasertown 3103 | 2024-07-22 18:14 | 45495.7597 | 2024-07-22 20:30 | 45495.8542 | 0.026111 | 0.00019199 | 5 | 680 | Unplanned | Unknown cause | Replaced fuses
404 |  | 3053A | Kanakanaia Rd Bruce Rd | Gisborne | Kanakanaia 1202 | 2024-07-23 08:30 | 45496.3542 | 2024-07-23 14:41 | 45496.6118 | 0.80866 | 0.0021887 | 57 | 10541.5262 | Planned | Planned | Remove ABS E318. Replace HV Links E135
405 |  | 7800 | 7078 Waiapu Road | Gisborne | Makarika 0204 | 2024-07-24 06:10 | 45497.2569 | 2024-07-24 08:05 | 45497.3368 | 0.0044158 | 3.8398e-05 | 1 | 115 | Unplanned | Unknown cause | Replaced fuses
406 |  | 3092 | Motu Road | Gisborne | Matawai 1204 | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 14:59 | 45497.6243 | 0.11949 | 0.00030718 | 8 | 1556.478 | Planned | Planned | Replace 11kV Poles
407 |  | 3085 | Waiomoko Rd Andrews Rd | Gisborne | Dalton 0502 | 2024-07-24 09:02 | 45497.3764 | 2024-07-24 15:52 | 45497.6611 | 0.33061 | 0.00080636 | 21 | 4308.4714 | Planned | Planned | Replace 11kV Poles
408 |  | 29218 | Te Hue Road | Gisborne | Awatere 0101 | 2024-07-25 09:01 | 45498.3757 | 2024-07-25 12:17 | 45498.5118 | 0.015052 | 7.6796e-05 | 2 | 392 | Unplanned | Defective Equipment | Replace pole J787 - Faulty x-arm
409 |  | 7401 | 2225 SH2 Whakaki | Wairoa | Nuhaka 3203 | 2024-07-25 18:29 | 45498.7701 | 2024-07-25 19:30 | 45498.8125 | 0.11946 | 0.0019583 | 51 | 3111 | Unplanned | Unknown cause | Replaced fuses
410 |  | N/A 22 | SH35 Whangara Road | Gisborne | Rototahi 0403 | 2024-07-26 00:49 | 45499.034 | 2024-07-26 01:55 | 45499.0799 | 0.5474 | 0.008294 | 216 | 14256 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct
411 |  | N/A 22 | SH35 Whangara Road | Gisborne | Town 0402 | 2024-07-26 00:49 | 45499.034 | 2024-07-26 02:05 | 45499.0868 | 0.59824 | 0.0078716 | 205 | 15580 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct
412 |  | N/A 22 | SH35 Whangara Road | Gisborne | Toko Tie 0401 | 2024-07-26 00:49 | 45499.034 | 2024-07-26 02:07 | 45499.0882 | 0.25158 | 0.0032254 | 84 | 6552 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct
413 |  | N/A 22 | SH35 Whangara Road | Gisborne | Tauwhareparae 0404 | 2024-07-26 00:49 | 45499.034 | 2024-07-26 02:11 | 45499.091 | 0.4597 | 0.0056061 | 146 | 11972 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct
414 |  | N/A 22 | SH35 Whangara Road | Gisborne | Tolaga Bay Sub | 2024-07-26 00:49 | 45499.034 | 2024-07-26 02:05 | 45499.0868 | 0.0029183 | 3.8398e-05 | 1 | 76 | Unplanned | Unknown cause | Daylight patrol Goodwin Rd - Tolaga Bay - Tokomaru Bay. Unable to identify obvious fault cause at accessible points. Restore supply to 50kV cct
415 |  | 3099 | Motu Road | Gisborne | Matawai 1204 | 2024-07-26 08:32 | 45499.3556 | 2024-07-26 13:36 | 45499.5667 | 0.093384 | 0.00030718 | 8 | 1216.4055 | Planned | Planned | Replace 11kV Poles
416 |  | 3098 | Bruce Road | Gisborne | Waimata 0903 | 2024-07-26 08:33 | 45499.3562 | 2024-07-26 09:33 | 45499.3979 | 0.020735 | 0.00034558 | 9 | 270.0933 | Planned | Planned | Shelterbelt clearing
417 |  | 5100B | Worsley Street | Gisborne | Tamarau 0503 | 2024-07-26 09:01 | 45499.3757 | 2024-07-26 14:38 | 45499.6097 | 1.3717 | 0.0040702 | 106 | 12718.5571 | Planned | Planned | Install new 11/400 Pole & TX A2475
418 |  | N/A 23 | Parkinson Sub | Gisborne | Solander 0706 | 2024-07-28 18:32 | 45501.7722 | 2024-07-28 19:35 | 45501.816 | 0.099182 | 0.0015743 | 41 | 2583 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause
419 |  | N/A 23 | Parkinson Sub | Gisborne | Cedenco A 0704 | 2024-07-28 18:32 | 45501.7722 | 2024-07-28 19:35 | 45501.816 | 0.0072572 | 0.00011519 | 3 | 189 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause
420 |  | N/A 23 | Parkinson Sub | Gisborne | Innes 0705 | 2024-07-28 18:32 | 45501.7722 | 2024-07-28 19:34 | 45501.8153 | 0.076182 | 0.0012287 | 32 | 1984 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause
421 |  | N/A 23 | Parkinson Sub | Gisborne | Chalmers 0707 | 2024-07-28 18:32 | 45501.7722 | 2024-07-28 19:33 | 45501.8146 | 1.6677 | 0.027339 | 712 | 43432 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause
422 |  | N/A 23 | Parkinson Sub | Gisborne | Lytton 0701 | 2024-07-28 18:32 | 45501.7722 | 2024-07-28 19:32 | 45501.8139 | 0.16358 | 0.0027263 | 71 | 4260 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause
423 |  | N/A 23 | Parkinson Sub | Gisborne | Willows 0702 | 2024-07-28 18:32 | 45501.7722 | 2024-07-28 19:31 | 45501.8132 | 0.18804 | 0.003187 | 83 | 4897 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause
424 |  | N/A 23 | Parkinson Sub | Gisborne | Elgin 0703 | 2024-07-28 18:32 | 45501.7722 | 2024-07-28 19:30 | 45501.8125 | 2.0511 | 0.035365 | 921 | 53418 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause
425 |  | N/A 23 | Parkinson Sub | Gisborne | JNL Sub 16 | 2024-07-28 18:32 | 45501.7722 | 2024-07-28 19:26 | 45501.8097 | 0.0020735 | 3.8398e-05 | 1 | 54 | Unplanned | Unknown cause | CB31=450a Bphase ER - No fault found. No obvious sign of cause
426 |  | 7411 | 385 Awamate Road | Wairoa | Raupunga 3101 | 2024-07-29 06:20 | 45502.2639 | 2024-07-29 07:20 | 45502.3056 | 0.036862 | 0.00061437 | 16 | 960 | Unplanned | Unknown cause | Replaced fuses
427 |  | 3100 | Kanakanaia Rd Waitangi Rd | Gisborne | Kanakanaia 1202 | 2024-07-30 08:30 | 45503.3542 | 2024-07-30 14:51 | 45503.6188 | 0.40963 | 0.0010751 | 28 | 5339.7348 | Planned | Planned | Replace 11kV poles - E1068
428 |  | 3093 | Waiomoko Road | Gisborne | Dalton 0502 | 2024-07-30 09:06 | 45503.3792 | 2024-07-30 15:05 | 45503.6285 | 0.12406 | 0.00034558 | 9 | 1616.0583 | Planned | Planned | Replace 11kV Poles
429 |  | 3107 | Nuhaka Opoutama Rd Waikokopu Rd Whaanga St Wai Station Rd | Wairoa | Nuhaka 3203 | 2024-07-30 09:07 | 45503.3799 | 2024-07-30 17:02 | 45503.7097 | 0.4195 | 0.00088315 | 23 | 5098.9992 | Planned | Planned | Replace 11kV poles
430 |  | 6681 | Maraehara Road | Gisborne | Tiki Tiki 0206 | 2024-07-30 10:30 | 45503.4375 | 2024-07-30 14:40 | 45503.6111 | 0.27839 | 0.0011135 | 29 | 7250 | Unplanned | Defective Equipment | Floating wire
431 |  | 29223 | Maraehara Road | Gisborne | Tiki Tiki 0206 | 2024-07-30 13:23 | 45503.5576 | 2024-07-30 14:45 | 45503.6146 | 0.091311 | 0.0011135 | 29 | 2378 | Unplanned | Defective Equipment | Insulator dislodged from x-arm on pole J2161
432 |  | 6682 | 2754 Ihungia road | Gisborne | Mata 0304 | 2024-07-30 13:40 | 45503.5694 | 2024-07-30 16:45 | 45503.6979 | 0.14918 | 0.00080636 | 21 | 3885 | Unplanned | Adverse Weather | Flooding/roads/traffic - bad weather
433 |  | N/A 24 | Mata Road | Gisborne | Mata 0304 | 2024-07-30 16:28 | 45503.6861 | 2024-07-30 16:44 | 45503.6972 | 0.018431 | 0.0011519 | 30 | 480 | Unplanned | Unknown cause | 1 HV fuse down @ H272 (Centry 0) Opened Sectionaliser to close fuses. Slosed Sectionaliser, fuses holding
434 |  | 3094 | Waiomoko Rd Wharekiri Rd | Gisborne | Dalton 0502 | 2024-07-31 09:06 | 45504.3792 | 2024-07-31 16:02 | 45504.6681 | 0.41531 | 0.00099835 | 26 | 5387.3731 | Planned | Planned | Replace 11kV poles - A3999, A4000, A4001, A4004
435 |  | 3106 | Lavenham Rd | Gisborne | Lavenham 0902 | 2024-07-31 09:15 | 45504.3854 | 2024-07-31 15:25 | 45504.6424 | 0.085244 | 0.00023039 | 6 | 1110.2557 | Planned | Planned | Replace 11kV Poles - D2001 - D390
436 |  | 3131 | Clyde Rd Brian Avenue Chamberlain Avenue | Wairoa | Borough One 3204 | 2024-07-31 15:34 | 45504.6486 | 2024-07-31 16:10 | 45504.6736 | 0.1175 | 0.0032638 | 85 | 3060 | Planned | Planned | Urgent Fault - To Repair neutral connections on TX W1579
437 |  | 3108 | Nuhaka - Opoutama Rd - Waikokopu Road | Wairoa | Morere 3401 | 2024-08-01 09:03 | 45505.3771 | 2024-08-01 15:25 | 45505.6424 | 0.33737 | 0.00088315 | 23 | 4396.8797 | Planned | Planned | Replace poles
438 |  | 29168/29169 | Waipiro Road | Gisborne | Inland 0301 | 2024-08-01 13:01 | 45505.5424 | 2024-08-02 16:22 | 45506.6819 | 0.16976 | 0.0024959 | 65 | 4421 | Unplanned | Vegetation | Tree through 11kV between poles H2224 & H2226
439 |  | 29167 | 43 Omana Road, Nuhaka | Wairoa | Morere 3401 | 2024-08-01 13:55 | 45505.5799 | 2024-08-01 14:42 | 45505.6125 | 0.0072188 | 0.00015359 | 4 | 188 | Unplanned | Vegetation | Tree contacted LV line from TX W7975 & Pole W20544. Wrapped conductor, Isolated from TX W7975
440 |  | 7412 | 145 Nuhaka Oputama Rd | Wairoa | Morere 3401 | 2024-08-01 21:22 | 45505.8903 | 2024-08-01 22:30 | 45505.9375 | 0.015666 | 0.00023039 | 6 | 408 | Unplanned | Unknown cause | Replaced TX fuse
441 |  | 7413 | 310 Kaiwaitau Road | Wairoa | Mahia 3301 | 2024-08-02 07:22 | 45506.3069 | 2024-08-02 09:40 | 45506.4028 | 0.18546 | 0.0013439 | 35 | 4830 | Unplanned | Unknown cause | Replaced fuses
442 |  | 3105 | Kanakanaia Rd Waitangi Rd | Gisborne | Kanakanaia 1202 | 2024-08-02 08:30 | 45506.3542 | 2024-08-02 15:52 | 45506.6611 | 0.47521 | 0.0010751 | 28 | 6194.653 | Planned | Planned | Replace poles
443 |  | 9306 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2024-08-02 08:36 | 45506.3583 | 2024-08-02 11:00 | 45506.4583 | 0.066352 | 0.00046078 | 12 | 1728 | Unplanned | Wildlife | Replaced fuses - HV fuses next to lake
444 |  | 3109 | Oak St, Elm Street | Gisborne | Gladstone 0607 | 2024-08-02 09:03 | 45506.3771 | 2024-08-02 16:09 | 45506.6729 | 0.78516 | 0.0018431 | 48 | 7141.1377 | Planned | Planned | Replace SW/GR
445 |  | 29170 | Managapa | Gisborne | Gladstone 0607 | 2024-08-03 08:05 | 45507.3368 | 2024-08-03 13:51 | 45507.5771 | 5.518 | 0.042391 | 1104 | 143705 | Unplanned | Unknown cause | Fault indicators indicated fault past B847, (new SW/GR) Patrolled nothing found - Switching incident
446 |  | N/A 25 | Coast | Gisborne | Tauwhareparae 0404 | 2024-08-03 09:15 | 45507.3854 | 2024-08-03 09:52 | 45507.4111 | 0.20743 | 0.0056061 | 146 | 5402 | Unplanned | Wildlife | Duck hit line
447 |  | N/A 25 | Coast | Gisborne | Toko Tie 0401 | 2024-08-03 09:15 | 45507.3854 | 2024-08-03 09:49 | 45507.409 | 0.10966 | 0.0032254 | 84 | 2856 | Unplanned | Wildlife | Duck hit line
448 |  | N/A 25 | Coast | Gisborne | Town 0402 | 2024-08-03 09:15 | 45507.3854 | 2024-08-03 09:48 | 45507.4083 | 0.25976 | 0.0078716 | 205 | 6765 | Unplanned | Wildlife | Duck hit line
449 |  | N/A 25 | Coast | Gisborne | Rototahi 0403 | 2024-08-03 09:15 | 45507.3854 | 2024-08-03 09:42 | 45507.4042 | 0.22497 | 0.0083324 | 217 | 5859 | Unplanned | Wildlife | Duck hit line
450 |  | N/A 26 | Wairoa Township | Wairoa | Borough Two 3205 | 2024-08-03 16:47 | 45507.6993 | 2024-08-03 18:16 | 45507.7611 | 1.4653 | 0.027339 | 712 | 38160 | Unplanned | Defective Equipment | Unknown - Later found cracked insulator & burnt x-arm - Pole W3017
451 |  | N/A 27 | Wairoa Township | Wairoa | Borough Two 3205 | 2024-08-04 02:33 | 45508.1062 | 2024-08-04 04:00 | 45508.1667 | 1.3882 | 0.025458 | 663 | 36153 | Unplanned | Defective Equipment | Not found, later found broken insulator/burnt x-arm
452 |  | 9307 | Ruakaka Road | Gisborne | Tiniroto 1003 | 2024-08-04 18:30 | 45508.7708 | 2024-08-04 21:00 | 45508.875 | 0.13247 | 0.00088315 | 23 | 3450 | Unplanned | Unknown cause | Replaced fuses
453 |  | 3095 | Panikau Road | Gisborne | Dalton 0502 | 2024-08-05 09:02 | 45509.3764 | 2024-08-05 16:15 | 45509.6771 | 0.14964 | 0.00034558 | 9 | 1881.65 | Planned | Planned | Replace poles
454 |  | 3114 | Kanakanaia Rd, Waitangi Rd | Gisborne | Kanakanaia 1202 | 2024-08-06 08:30 | 45510.3542 | 2024-08-06 14:23 | 45510.5993 | 0.37953 | 0.0010751 | 28 | 4947.3134 | Planned | Planned | Replace 11kV poles
455 |  | 29234 | Rutherford Street, Tawhara Valley Rd | Wairoa | Borough Two 3205 | 2024-08-06 10:22 | 45510.4319 | 2024-08-06 13:59 | 45510.5826 | 0.16665 | 0.00076796 | 20 | 4340 | Unplanned | Defective Equipment | Replaced pole W3017. Boro 2 had been faulting suspect this was our fault.
456 |  | 3116 | Mata Road, Ihungia Rd | Gisborne | Mata 0304 | 2024-08-07 09:00 | 45511.375 | 2024-08-07 16:21 | 45511.6813 | 0.55881 | 0.0012671 | 33 | 6938.7812 | Planned | Planned | Replace 11kV Poles
457 |  | 3097 | Panikau Road | Gisborne | Dalton 0502 | 2024-08-07 09:03 | 45511.3771 | 2024-08-07 16:16 | 45511.6778 | 0.14964 | 0.00034558 | 9 | 1877.1485 | Planned | Planned | Replace 11kV poles
458 |  | 3115 | Kanakanaia Rd, Waitangi Rd | Gisborne | Kanakanaia 1202 | 2024-08-08 08:30 | 45512.3542 | 2024-08-08 15:57 | 45512.6646 | 0.48059 | 0.0010751 | 28 | 6264.7283 | Planned | Planned | Replace 11kV poles. Install HV fuses E1107 & E957. Remove HV fuses E142 & E148
459 |  | 3103A | Goodwin Road | Gisborne | Whangara 0506 | 2024-08-08 09:02 | 45512.3764 | 2024-08-08 13:53 | 45512.5785 | 0.61456 | 0.0021119 | 55 | 16005 | Planned | Planned | Replace TX pole A88
460 |  | 3091A | Pakowhai Rd | Gisborne | Muriwai 0905 | 2024-08-09 08:41 | 45513.3618 | 2024-08-09 11:10 | 45513.4653 | 0.091541 | 0.00061437 | 16 | 2384 | Unplanned | Human Error | Outage in place to allow for bridge installation in close proximity to OH 11kV. Note: Only had 1 day notice from bridge contractor of wanting shutdown that was deferred earlier in July
461 |  | 3102 | Panikau Road | Gisborne | Dalton 0502 | 2024-08-09 09:03 | 45513.3771 | 2024-08-09 16:09 | 45513.6729 | 0.49073 | 0.0011519 | 30 | 6262.2054 | Planned | Planned | Replace 11kV poles
462 |  | 3125A | 113 Whatatutu Road | Gisborne | Matawai 1204 | 2024-08-09 09:32 | 45513.3972 | 2024-08-09 11:15 | 45513.4688 | 0.00791 | 7.6796e-05 | 2 | 206 | Planned | Planned | Upgrade TX F273
463 |  | 3126A | 113 Whatatutu Road | Gisborne | Whatatutu 1201 | 2024-08-09 11:41 | 45513.4868 | 2024-08-09 14:35 | 45513.6076 | 0.033406 | 0.00019199 | 5 | 870 | Planned | Planned | Upgrade TX F447
464 |  | 29243 | Ardkeen, Ruapapa, Cricklewood | Wairoa | Frasertown 3103 | 2024-08-10 00:42 | 45514.0292 | 2024-08-10 14:54 | 45514.6208 | 2.4908 | 0.0067581 | 176 | 64867 | Unplanned | Vegetation | Tree across 50kV / 11kV @ Pole W4775. 11kV conductor damaged
465 |  | 3117 | Pitchers Road | Gisborne | Te Karaka 1203 | 2024-08-10 09:12 | 45514.3833 | 2024-08-10 11:47 | 45514.491 | 0.041662 | 0.00026879 | 7 | 542.6458 | Planned | Planned | Cutover 11kV OH to U/ground and connect to RMU E876
466 |  | 8116 | 361 Waiapu Road | Gisborne | Toko Tie 0401 | 2024-08-10 10:21 | 45514.4313 | 2024-08-10 12:30 | 45514.5208 | 0.0099067 | 7.6796e-05 | 2 | 258 | Unplanned | Lightning | Lightning storm
467 |  | 8117 | 838 Paroa Road | Gisborne | Toko Tie 0401 | 2024-08-10 11:19 | 45514.4715 | 2024-08-10 13:15 | 45514.5521 | 0.0044542 | 3.8398e-05 | 1 | 116 | Unplanned | Lightning | Lightning storm
468 |  | 8118 | 601 Waiapu Rd | Gisborne | Toko Tie 0401 | 2024-08-10 13:35 | 45514.566 | 2024-08-10 15:30 | 45514.6458 | 0.013247 | 0.00011519 | 3 | 345 | Unplanned | Lightning | Lightning storm
469 |  | 29244 | Humphrey Road | Gisborne | Lavenham 0902 | 2024-08-10 14:14 | 45514.5931 | 2024-08-10 15:09 | 45514.6312 | 0.014783 | 0.00026879 | 7 | 385 | Unplanned | Defective Equipment | DDO fuse @ HV fuses D3029 required replacement
470 |  | 8119 | 14 Ruakaka Road | Gisborne | Tiniroto 1003 | 2024-08-11 07:45 | 45515.3229 | 2024-08-11 09:15 | 45515.3854 | 0.048382 | 0.00053757 | 14 | 1260 | Unplanned | Unknown cause | Replaced fuses
471 |  | 8120 | 77 Wharekaka Road | Gisborne | Toko Tie 0401 | 2024-08-11 17:51 | 45515.7438 | 2024-08-11 18:30 | 45515.7708 | 0.002995 | 7.6796e-05 | 2 | 78 | Unplanned | Unknown cause | Replaced glass fuse
472 |  | 29245 | Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2024-08-11 19:31 | 45515.8132 | 2024-08-12 11:46 | 45516.4903 | 0.39174 | 0.00046078 | 12 | 10202 | Unplanned | Wildlife | Possum on pole
473 |  | 7192 | Wharekaka Road | Gisborne | Toko Tie 0401 | 2024-08-12 13:13 | 45516.5507 | 2024-08-12 16:30 | 45516.6875 | 0.0075644 | 3.8398e-05 | 1 | 197 | Unplanned | Unknown cause | Replace fuses
474 |  | 29183 | Whakaki | Wairoa | Nuhaka 3203 | 2024-08-12 19:05 | 45516.7951 | 2024-08-13 19:05 | 45517.7951 | 1.6716 | 0.011942 | 311 | 43533 | Unplanned | Vegetation | Tree thru line broke x-arm. No backfeed. See Tahanui Fault #2
475 |  | 29182 | Nuhaka | Wairoa | Morere 3401 | 2024-08-12 19:19 | 45516.8049 | 2024-08-12 22:38 | 45516.9431 | 1.8269 | 0.010291 | 268 | 47578 | Unplanned | Defective Equipment | Broken conductor - High winds
476 |  | 29248 | Taurau Valley Road | Gisborne | Te Arai 0906 | 2024-08-12 19:21 | 45516.8063 | 2024-08-15 11:55 | 45519.4965 | 1.1062 | 0.01797 | 468 | 28810 | Unplanned | Defective Equipment | Pole C2662 snapped @ ground level during high winds
477 |  | N/A 29 | Ohuka | Wairoa | Ruakituri 2003 | 2024-08-12 19:25 | 45516.809 | 2024-08-12 20:52 | 45516.8694 | 0.38986 | 0.004723 | 123 | 10153 | Unplanned | Adverse Weather | High wind through region during this period
478 |  | 29249 | Maungataniwha | Wairoa | Raupunga 3101 | 2024-08-12 19:35 | 45516.816 | 2024-08-13 15:38 | 45517.6514 | 1.2339 | 0.0059517 | 155 | 32135 | Unplanned | Vegetation | Tree through line W5127 - W5128 - See Fault 6
479 |  | 3120 | Motu Road | Gisborne | Matawai 1204 | 2024-08-13 08:30 | 45517.3542 | 2024-08-13 14:08 | 45517.5889 | 0.10383 | 0.00030718 | 8 | 1352.4153 | Planned | Planned | Replace 11kV Poles
480 |  | 29247 | Manuka & Tutara Street | Gisborne | Elgin 0703 | 2024-08-13 08:41 | 45517.3618 | 2024-08-14 16:46 | 45518.6986 | 3.0445 | 0.039051 | 1017 | 79287 | Unplanned | Defective Equipment | Cable term at B1430, then cable fault Manuka St (Jnt)
481 |  | 29187 | Mahanga Rd | Wairoa | Mahia 3301 | 2024-08-13 11:00 | 45517.4583 | 2024-08-14 14:03 | 45518.5854 | 1.9611 | 0.0056061 | 146 | 51072 | Unplanned | Vegetation | Replace 11kV pole W9196 & remove tree from 11kV. Broke x-arm
482 |  | N/A 28 | Tahaenui, Mahia | Wairoa | Mahia 3301 | 2024-08-13 14:07 | 45517.5882 | 2024-08-13 16:03 | 45517.6687 | 4.0249 | 0.063434 | 1652 | 104820 | Unplanned | Adverse Weather | High winds through region during this day. Potential line clash - High. Generator failed. Fault at Iwetea, No back feed.
483 |  | N/A 28 | Tahaenui, Mahia | Wairoa | Nuhaka 3203 | 2024-08-13 14:07 | 45517.5882 | 2024-08-13 15:34 | 45517.6486 | 0.24387 | 0.0028031 | 73 | 6351 | Unplanned | Adverse Weather | High winds through region during this day. Potential line clash - High. Generator failed. Fault at Iwetea, No back feed.
484 |  | N/A 28 | Tahaenui, Mahia | Wairoa | Morere 3401 | 2024-08-13 14:07 | 45517.5882 | 2024-08-13 15:34 | 45517.6486 | 0.88527 | 0.010175 | 265 | 23055 | Unplanned | Adverse Weather | High winds through region during this day. Potential line clash - High. Generator failed. Fault at Iwetea, No back feed.
485 |  | 7414 | 217 Preston Rd | Wairoa | Morere 3401 | 2024-08-13 15:49 | 45517.659 | 2024-08-14 13:00 | 45518.5417 | 0.58565 | 0.00046078 | 12 | 15252 | Unplanned | Adverse Weather | Replaced fuse
486 |  | 3123 | Waimata Valley Rd | Gisborne | Waimata 0903 | 2024-08-14 08:33 | 45518.3562 | 2024-08-14 15:30 | 45518.6458 | 0.20816 | 0.00049917 | 13 | 2711.853 | Planned | Planned | Relocate TX E281
487 |  | 7193 | 3321 Wharerata Road | Gisborne | Muriwai 0905 | 2024-08-14 16:37 | 45518.6924 | 2024-08-14 20:30 | 45518.8542 | 0.017893 | 7.6796e-05 | 2 | 466 | Unplanned | Adverse Weather | Replace fuses
488 |  | 6684 | 4988 Te Araroa Road | Gisborne | Hicks Bay 0102 | 2024-08-15 08:14 | 45519.3431 | 2024-08-15 11:45 | 45519.4896 | 0.024306 | 0.00011519 | 3 | 633 | Unplanned | Adverse Weather | High Winds
489 |  | 3121 | Motu Road | Gisborne | Matawai 1204 | 2024-08-15 08:30 | 45519.3542 | 2024-08-15 13:14 | 45519.5514 | 0.08724 | 0.00030718 | 8 | 1136.4055 | Planned | Planned | Replace 11kV poles
490 |  | 29192 | Rangiahuia Road | Wairoa | Frasertown 3103 | 2024-08-15 09:33 | 45519.3979 | 2024-08-15 11:22 | 45519.4736 | 0.31817 | 0.0039166 | 102 | 8286 | Unplanned | Defective Equipment | Blown lightning Arrestor TX W1651
491 |  | 6685 | 40 Puia Street | Gisborne | Inland 0301 | 2024-08-15 10:00 | 45519.4167 | 2024-08-15 14:15 | 45519.5938 | 0.029374 | 0.00011519 | 3 | 765 | Unplanned | Adverse Weather | High Winds
492 |  | 29193 | Tuai | Wairoa | Village 2002 | 2024-08-15 12:56 | 45519.5389 | 2024-08-15 14:38 | 45519.6097 | 0.40341 | 0.003955 | 103 | 10506 | Unplanned | Vegetation | Conductor damaged with tree through line
493 |  | 29188 | 4185 SH 2 Raupunga | Wairoa | Raupunga 3101 | 2024-08-15 15:47 | 45519.6576 | 2024-08-15 16:47 | 45519.6993 | 0.13132 | 0.0021887 | 57 | 3420 | Unplanned | Vegetation | High Winds brought down tree throu lines
494 |  | 6686 | 535 Matahiia Road | Gisborne | Makarika 0204 | 2024-08-15 16:28 | 45519.6861 | 2024-08-15 18:20 | 45519.7639 | 0.051607 | 0.00046078 | 12 | 1344 | Unplanned | Defective Equipment | Live wire against x-arm broken - replaced 16/8/24
495 |  | 29261 | Matahiia Road | Gisborne | Makarika 0204 | 2024-08-15 17:16 | 45519.7194 | 2024-08-16 16:03 | 45520.6687 | 0.35295 | 0.00069116 | 18 | 9192 | Unplanned | Defective Equipment | Replace Pole H1644 and rejoin 11kV line break
496 |  | 7415 | 35 Aranui Road | Wairoa | Raupunga 3101 | 2024-08-15 19:50 | 45519.8264 | 2024-08-15 21:00 | 45519.875 | 0.043006 | 0.00061437 | 16 | 1120 | Unplanned | Unknown cause | Replaced fuse
497 |  | 29264 | Matawai Road | Gisborne | Waimata 0903 | 2024-08-16 02:16 | 45520.0944 | 2024-08-16 14:13 | 45520.5924 | 0.80225 | 0.0049917 | 130 | 20893 | Unplanned | Third Party Interference | MVA @ Pole E2052. Isolated to allow crane to raise 11kV conductor/pole
498 |  | 3112 | Titarangi Rd Jackson Rd | Wairoa | Frasertown 3103 | 2024-08-16 09:05 | 45520.3785 | 2024-08-16 12:48 | 45520.5333 | 0.137 | 0.00061437 | 16 | 3568 | Planned | Planned | Replace 11kV Poles
499 |  | 29267 | Paroa Road | Gisborne | Toko Tie 0401 | 2024-08-16 11:03 | 45520.4604 | 2024-08-16 12:23 | 45520.516 | 0.0061437 | 7.6796e-05 | 2 | 160 | Unplanned | Defective Equipment | Repair LV fault, high winds
500 |  | 3127 | Frasertown Road | Wairoa | Nuhaka 3203 | 2024-08-16 11:05 | 45520.4618 | 2024-08-16 12:56 | 45520.5389 | 0.18327 | 0.0016511 | 43 | 1830.5174 | Planned | Planned | Replace Stub Pole damaged in MVA earlier
501 |  | 7195 | 14 Ruakaka Road | Gisborne | Tiniroto 1003 | 2024-08-17 14:05 | 45521.5868 | 2024-08-17 16:00 | 45521.6667 | 0.061821 | 0.00053757 | 14 | 1610 | Unplanned | Wildlife | Replace fuses
502 |  | 29302 | Wharerata / Bartletts | Gisborne | Muriwai 0905 | 2024-08-18 00:29 | 45522.0201 | 2024-08-18 02:42 | 45522.1125 | 0.68433 | 0.0051453 | 134 | 17822 | Unplanned | Defective Equipment | Broken polymer strain - conductor crossed over BC phases. C3514 - C659
503 |  | 29310 | Tikitiki | Gisborne | Tiki Tiki 0206 | 2024-08-18 02:01 | 45522.084 | 2024-08-19 17:12 | 45523.7167 | 10.8318 | 0.020044 | 522 | 282093 | Unplanned | Vegetation | Trees thru lines J2320 - J2319
504 |  | 29327 | Poroporo Valley Road | Gisborne | Tiki Tiki 0206 | 2024-08-18 05:39 | 45522.2354 | 2024-08-21 14:22 | 45525.5986 | 2.4175 | 0.00049917 | 13 | 62959 | Unplanned | Vegetation | Tree thru line J1003 - J1004
505 |  | 29334 | Eastcape Lighthouse | Gisborne | Tiki Tiki 0206 | 2024-08-18 05:39 | 45522.2354 | 2024-08-21 14:17 | 45525.5951 | 1.3004 | 0.00026879 | 7 | 33866 | Unplanned | Vegetation | Tree thru line. Hi winds. J2508 - J248
506 |  | 29303 | Tahora | Gisborne | Tahora 1103 | 2024-08-18 06:47 | 45522.2826 | 2024-08-18 11:25 | 45522.4757 | 1.1301 | 0.0057597 | 150 | 29432 | Unplanned | Vegetation | Tree through 11kV lind @ pole D2921
507 |  | 29332 | Tuakau / Ihungia | Gisborne | Mata 0304 | 2024-08-18 07:17 | 45522.3035 | 2024-08-21 15:23 | 45525.641 | 1.8645 | 0.00061437 | 16 | 48557 | Unplanned | Vegetation | Tree thru line x 3. See #12 & #15 No Backfeed
508 |  | N/A 30 | Awatere | Gisborne | Awatere 0101 | 2024-08-18 07:47 | 45522.3243 | 2024-08-18 08:08 | 45522.3389 | 0.057251 | 0.0027263 | 71 | 1491 | Unplanned | Adverse Weather | Highwind in area. J2756 in open position see #3
509 |  | 7421 | Ohuka Road | Wairoa | Ruakituri 2003 | 2024-08-18 08:13 | 45522.3424 | 2024-08-18 11:00 | 45522.4583 | 0.17955 | 0.0010751 | 28 | 4676 | Unplanned | Adverse Weather | Replaced fuses - wind
510 |  | 29305 | Ruatoria | Gisborne | Ruatoria 0201 | 2024-08-18 08:22 | 45522.3486 | 2024-08-20 14:03 | 45524.5854 | 1.1007 | 0.015052 | 392 | 28666 | Unplanned | Vegetation | Trees thru conductor, High wind - J1386 - J1385
511 |  | 9310 | Kanakania Road | Gisborne | Kanakanaia 1202 | 2024-08-18 08:24 | 45522.35 | 2024-08-19 16:30 | 45523.6875 | 0.51768 | 0.00026879 | 7 | 13482 | Unplanned | Vegetation | Replaced HV fuses
512 |  | 29272 | Panikau | Gisborne | Dalton 0502 | 2024-08-18 08:40 | 45522.3611 | 2024-08-20 14:33 | 45524.6062 | 2.3386 | 0.0028799 | 75 | 60904 | Unplanned | Vegetation | Tree thru line
513 |  | N/A 34 | Coast | Gisborne | Te Araroa Sub 01 | 2024-08-18 09:18 | 45522.3875 | 2024-08-18 10:01 | 45522.4174 | 0.0016511 | 3.8398e-05 | 1 | 43 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22
514 |  | N/A 34 | Coast | Gisborne | Awatere 0101 | 2024-08-18 09:18 | 45522.3875 | 2024-08-18 10:01 | 45522.4174 | 0.15025 | 0.0034942 | 91 | 3913 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22
515 |  | N/A 34 | Coast | Gisborne | Hicks Bay 0102 | 2024-08-18 09:18 | 45522.3875 | 2024-08-18 10:01 | 45522.4174 | 0.42269 | 0.0098299 | 256 | 11008 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22
516 |  | N/A 34 | Coast | Gisborne | Te Araroa 0103 | 2024-08-18 09:18 | 45522.3875 | 2024-08-18 10:01 | 45522.4174 | 0.21299 | 0.0049533 | 129 | 5547 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22
517 |  | N/A 34 | Coast | Gisborne | Ruatoria Sub 02 | 2024-08-18 09:18 | 45522.3875 | 2024-08-18 10:04 | 45522.4194 | 0.0017663 | 3.8398e-05 | 1 | 46 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22
518 |  | N/A 34 | Coast | Gisborne | Ruatoria 0201 | 2024-08-18 09:18 | 45522.3875 | 2024-08-18 13:52 | 45522.5778 | 1.1354 | 0.023653 | 616 | 29568 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22
519 |  | N/A 34 | Coast | Gisborne | Makarika 0204 | 2024-08-18 09:18 | 45522.3875 | 2024-08-18 10:04 | 45522.4194 | 0.19959 | 0.004339 | 113 | 5198 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22
520 |  | N/A 34 | Coast | Gisborne | Tiki Tiki 0206 | 2024-08-18 09:18 | 45522.3875 | 2024-08-18 18:41 | 45522.7785 | 4.65 | 0.024268 | 632 | 121100 | Unplanned | Vegetation | Tree thru line - High winds. See #11 & #15 & #22
521 |  | 7416 | 2026 Waihi Road | Wairoa | Frasertown 3103 | 2024-08-18 10:15 | 45522.4271 | 2024-08-18 14:30 | 45522.6042 | 0.029374 | 0.00011519 | 3 | 765 | Unplanned | Adverse Weather | Replace isolation fuse
522 |  | 29309 | Waiapu Rd / Mangatuna Road | Gisborne | Toko Tie 0401 | 2024-08-18 11:34 | 45522.4819 | 2024-08-18 20:50 | 45522.8681 | 0.78121 | 0.0032254 | 84 | 20345 | Unplanned | Defective Equipment | Centre bolt failed, tripped x-arm
523 |  | 29311 | Turihau | Gisborne | Dalton 0502 | 2024-08-18 11:44 | 45522.4889 | 2024-08-19 17:23 | 45523.7243 | 3.4483 | 0.0091387 | 238 | 89804 | Unplanned | Adverse Weather | Wind broke conductor A4441 - A4441. No Backfeed, see #10 & #17. See #10 Wharikiri Rd off
524 |  | 29307 | Waimata Valley Road | Gisborne | Waimata 0903 | 2024-08-18 12:03 | 45522.5021 | 2024-08-20 12:06 | 45524.5042 | 0.78797 | 0.003571 | 93 | 20521 | Unplanned | Vegetation | Tree thru line. Fault #10 meant no Backfeed
525 |  | 29269 | Te Puia | Gisborne | Inland 0301 | 2024-08-18 12:32 | 45522.5222 | 2024-08-19 14:13 | 45523.5924 | 8.3866 | 0.0061437 | 160 | 218412 | Unplanned | Vegetation | Tree thru line - High Winds
526 |  | 29316 | Tauwhareparau | Gisborne | Tauwhareparae 0404 | 2024-08-18 12:46 | 45522.5319 | 2024-08-21 18:49 | 45525.784 | 4.9239 | 0.011059 | 288 | 128234 | Unplanned | Defective Equipment | Broken pole due to high winds G2265 plus tree thru line G2509
527 |  | 29308 | Rototahi | Gisborne | Rototahi 0403 | 2024-08-18 12:48 | 45522.5333 | 2024-08-19 10:49 | 45523.4507 | 3.213 | 0.008294 | 216 | 83676 | Unplanned | Vegetation | Tree thru line, no back feed. Turihau Fault #13 & #19
528 |  | 7417 | 44 Ngamotu Road | Wairoa | Affco 3202 | 2024-08-18 12:52 | 45522.5361 | 2024-08-18 16:30 | 45522.6875 | 0.25949 | 0.0011903 | 31 | 6758 | Unplanned | Adverse Weather | Replaced fuse
529 |  | 29313 | Makarika | Gisborne | Makarika 0204 | 2024-08-18 13:02 | 45522.5431 | 2024-08-19 18:53 | 45523.7868 | 6.7753 | 0.004339 | 113 | 176448 | Unplanned | Vegetation | Tree thru line - High winds. No back feeds. See #15 & #11 & #9
530 |  | 29315 | Mata Rd / Waiapu Road | Gisborne | Mata 0304 | 2024-08-18 13:24 | 45522.5583 | 2024-08-19 16:37 | 45523.6924 | 3.8273 | 0.0099067 | 258 | 99674 | Unplanned | Vegetation | Tree thru line @ H3527
531 |  | N/A 32 | Coast | Gisborne | Town 0402 | 2024-08-18 13:33 | 45522.5646 | 2024-08-18 14:21 | 45522.5979 | 0.37784 | 0.0078716 | 205 | 9840 | Unplanned | Adverse Weather | High Winds. Tauwharepara G327 open see #16 Toko Open #12
532 |  | 29312 | Frasertown Road / Awatere Road | Wairoa | Nuhaka 3203 | 2024-08-18 21:08 | 45522.8806 | 2024-08-18 21:37 | 45522.9007 | 0.014476 | 0.00049917 | 13 | 377 | Unplanned | Adverse Weather | High Winds broke Conductor
533 |  | 9405 | Te Wera Road | Gisborne | Matawai 1204 | 2024-08-19 07:01 | 45523.2924 | 2024-08-19 18:00 | 45523.75 | 0.27835 | 0.00042238 | 11 | 7249 | Unplanned | Adverse Weather | Replaced fuses
534 |  | 9308 | Mangamaia Road | Gisborne | Whatatutu 1201 | 2024-08-19 07:15 | 45523.3021 | 2024-08-19 12:30 | 45523.5208 | 0.30238 | 0.00095995 | 25 | 7875 | Unplanned | Adverse Weather | Replaced HV fuses
535 |  | 29295 | Te Araroa Substation, All feeders. Sub on Generator | Gisborne | Te Araroa Sub 01 | 2024-08-19 07:32 | 45523.3139 | 2024-08-19 16:22 | 45523.6819 | 1.5779 | 0.035595 | 927 | 41093 | Unplanned | Vegetation | 4 spans of conductor down @ pole J324
536 |  | 9404 | Waingake Road | Gisborne | Te Arai 0906 | 2024-08-19 10:43 | 45523.4465 | 2024-08-20 14:30 | 45524.6042 | 0.32005 | 0.00019199 | 5 | 8335 | Unplanned | Adverse Weather | Replaced fuses
537 |  | N/A 31 | Ohuka | Wairoa | Ruakituri 2003 | 2024-08-19 13:03 | 45523.5437 | 2024-08-19 13:57 | 45523.5813 | 0.058058 | 0.0010751 | 28 | 1512 | Unplanned | Adverse Weather | Intial fault caused by PVT pole fault. 2nd Fault not found
538 |  | 29319 | Charteris Rise | Gisborne | Nelson 0803 | 2024-08-19 16:26 | 45523.6847 | 2024-08-20 11:53 | 45524.4951 | 0.010598 | 0.0017663 | 46 | 276 | Unplanned | Defective Equipment | Faulty cable term up pole. Install generator
539 |  | 9311 | Rakaroa Road | Gisborne | Whatatutu 1201 | 2024-08-19 16:30 | 45523.6875 | 2024-08-19 19:00 | 45523.7917 | 0.13823 | 0.00092155 | 24 | 3600 | Unplanned | Adverse Weather | Replaced HV fuses
540 |  | 29276 | Waiapu Road | Gisborne | Mata 0304 | 2024-08-19 17:00 | 45523.7083 | 2024-08-19 18:51 | 45523.7854 | 0.012787 | 0.00011519 | 3 | 333 | Unplanned | Defective Equipment | Broken Pole , High Winds H621
541 |  | 29328 | Waione Road | Gisborne | Awatere 0101 | 2024-08-19 17:30 | 45523.7292 | 2024-08-20 18:21 | 45524.7646 | 0.85877 | 0.00057597 | 15 | 22365 | Unplanned | Vegetation | Tree in line
542 |  | 29331 | Waitahia | Gisborne | Mata 0304 | 2024-08-19 17:30 | 45523.7292 | 2024-08-22 15:14 | 45526.6347 | 1.3165 | 0.00080636 | 21 | 34286 | Unplanned | Defective Equipment | Replace burning pole. High winds broke binder wire off insulator
543 |  | 29325 | Ruatoria | Gisborne | Ruatoria 0201 | 2024-08-19 18:05 | 45523.7535 | 2024-08-20 17:24 | 45524.725 | 0.10598 | 0.0033022 | 86 | 2760 | Unplanned | Defective Equipment | Repair Faulty ABS J622. Cracked Insulator faulm type
544 |  | 29278 | Kotemaori | Wairoa | Raupunga 3101 | 2024-08-19 19:34 | 45523.8153 | 2024-08-19 20:13 | 45523.8424 | 0.0059901 | 0.00015359 | 4 | 156 | Unplanned | Vegetation | Tree through LV supplied by TX W595
545 |  | 9312 | Ruakaka Road | Gisborne | Tiniroto 1003 | 2024-08-19 20:03 | 45523.8354 | 2024-08-20 12:30 | 45524.5208 | 0.87167 | 0.00088315 | 23 | 22701 | Unplanned | Adverse Weather | Replace fuses
546 |  | 9403 | Paparatu | Gisborne | Te Arai 0906 | 2024-08-19 21:38 | 45523.9014 | 2024-08-20 14:00 | 45524.5833 | 0.60331 | 0.00061437 | 16 | 15712 | Unplanned | Adverse Weather | Replaced ddo fuses
547 |  | 29317 | Ngatapa Sub | Gisborne | Tahora 1103 | 2024-08-20 05:03 | 45524.2104 | 2024-08-20 05:40 | 45524.2361 | 0.21453 | 0.0057981 | 151 | 5587 | Unplanned | Wildlife | Intertrip D31 - D13 appears due to OC trip CB D15. Bird strikes - Turkey
548 |  | 29317 | Ngatapa Sub | Gisborne | Ngatapa 1102 | 2024-08-20 05:03 | 45524.2104 | 2024-08-20 05:39 | 45524.2354 | 0.096763 | 0.0026879 | 70 | 2520 | Unplanned | Wildlife | Intertrip D31 - D13 appears due to OC trip CB D15. Bird strikes - Turkey
549 |  | 29317 | Ngatapa Sub | Gisborne | Totangi 1101 | 2024-08-20 05:03 | 45524.2104 | 2024-08-20 10:00 | 45524.4167 | 0.15966 | 0.00053757 | 14 | 4158 | Unplanned | Wildlife | Intertrip D31 - D13 appears due to OC trip CB D15. Bird strikes - Turkey
550 |  | 29317 | Ngatapa Sub | Gisborne | Ngatapa Sub 11 | 2024-08-20 05:03 | 45524.2104 | 2024-08-20 05:34 | 45524.2319 | 0.0011903 | 3.8398e-05 | 1 | 31 | Unplanned | Wildlife | Intertrip D31 - D13 appears due to OC trip CB D15. Bird strikes - Turkey
551 |  | 29281 | SH 35 | Gisborne | Tiki Tiki 0206 | 2024-08-20 10:48 | 45524.45 | 2024-08-20 17:12 | 45524.7167 | 0.17348 | 0.00069116 | 18 | 4518 | Unplanned | Defective Equipment | Replaced 11kV Pole J2383. Repair 11kV conductor
552 |  | 29290 | Waihi Rd | Wairoa | Frasertown 3103 | 2024-08-20 15:45 | 45524.6562 | 2024-08-20 16:45 | 45524.6979 | 0.025343 | 0.00042238 | 11 | 660 | Unplanned | Defective Equipment | Broken Jumper
553 |  | 29293 | Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2024-08-20 17:43 | 45524.7382 | 2024-08-22 15:10 | 45526.6319 | 0.8203 | 0.00046078 | 12 | 21363 | Unplanned | Vegetation | Replaced pole damaged by tree. Multiple faults on at same time
554 |  | 3118 | Andrews Rd Waiomoko Rd | Gisborne | Dalton 0502 | 2024-08-22 09:14 | 45526.3847 | 2024-08-22 14:09 | 45526.5896 | 0.033982 | 0.00011519 | 3 | 442.557 | Planned | Planned | Replace 11kV poles
555 |  | 9314 | Lake Road | Gisborne | Lavenham 0902 | 2024-08-22 10:57 | 45526.4563 | 2024-08-22 15:00 | 45526.625 | 0.055984 | 0.00023039 | 6 | 1458 | Unplanned | Wildlife | Replace fuses
556 |  | 7420 | 14 Spence Road, Te Ringa | Wairoa | Ruakituri 2003 | 2024-08-23 07:23 | 45527.3076 | 2024-08-23 09:00 | 45527.375 | 0.037246 | 0.00038398 | 10 | 970 | Unplanned | Unknown cause | Replaced fuse
557 |  | 3138 | Rakauroa Rd Tahora Rd Shaw Rd | Gisborne | Matawai 1204 | 2024-08-23 08:57 | 45527.3729 | 2024-08-23 10:59 | 45527.4576 | 0.070268 | 0.00057597 | 15 | 916.4255 | Planned | Planned | Replace TX F186
558 |  | 3119 | Andrews Rd Waiomoko Rd | Gisborne | Whangara 0506 | 2024-08-23 09:03 | 45527.3771 | 2024-08-23 14:40 | 45527.6111 | 0.03882 | 0.00011519 | 3 | 505.5582 | Planned | Planned | Replace Poles
559 |  | 29300 | Popoporo Valley | Gisborne | Tiki Tiki 0206 | 2024-08-23 11:24 | 45527.475 | 2024-08-23 14:23 | 45527.5993 | 0.089352 | 0.00049917 | 13 | 2327 | Unplanned | Defective Equipment | High Winds blew pole on 45deg lean. Straighten
560 |  | 9315 | Te Wera Road | Gisborne | Matawai 1204 | 2024-08-23 12:36 | 45527.525 | 2024-08-23 18:30 | 45527.7708 | 0.14952 | 0.00042238 | 11 | 3894 | Unplanned | Defective Equipment | Replace HV fuse
561 |  | 3130 | Potae St Beach Rd Tokomaru St Waima St Hikirangi St | Gisborne | Seaside 0302 | 2024-08-24 09:02 | 45528.3764 | 2024-08-24 13:07 | 45528.5465 | 1.0536 | 0.0043006 | 112 | 13792.2497 | Planned | Planned | Tree Cutting
562 |  | 29359 | Waitahia | Gisborne | Mata 0304 | 2024-08-25 11:09 | 45529.4646 | 2024-08-25 12:55 | 45529.5382 | 0.016281 | 0.00015359 | 4 | 424 | Unplanned | Defective Equipment | High winds broke binder
563 |  | 29360 | Goodwin Road | Gisborne | Whangara 0506 | 2024-08-25 19:00 | 45529.7917 | 2024-08-25 19:42 | 45529.8208 | 0.088469 | 0.0021119 | 55 | 2304 | Unplanned | Defective Equipment | Broken jumper on A87
564 |  | 29362 | Hiruharama Road | Gisborne | Makarika 0204 | 2024-08-25 19:08 | 45529.7972 | 2024-08-26 12:23 | 45530.516 | 0.51204 | 0.004339 | 113 | 13335 | Unplanned | Vegetation | Tree across line @ pole H241. Tree team arranged for 26/8
565 |  | 3144 | Riverside Rd Goodwin Rd | Gisborne | Whangara 0506 | 2024-08-26 09:03 | 45530.3771 | 2024-08-26 13:41 | 45530.5701 | 0.58711 | 0.0021119 | 55 | 7661.1454 | Planned | Planned | To install sectionaliser controls onto A91
566 |  | 29361 | Wharf Road | Gisborne | Rototahi 0403 | 2024-08-26 10:51 | 45530.4521 | 2024-08-26 12:04 | 45530.5028 | 0.044849 | 0.00061437 | 16 | 1168 | Unplanned | Third Party Interference | Replace pole G2678 (car V's pole over weekend)
567 |  | 29401 | Mata Road | Gisborne | Mata 0304 | 2024-08-26 11:17 | 45530.4701 | 2024-08-26 11:50 | 45530.4931 | 0.029144 | 0.00088315 | 23 | 759 | Unplanned | Defective Equipment | Repair blown jumper on ABS H179. High Winds
568 |  | 3148 | Waikura Valley Rd Te Kumi Rd | Gisborne | Hicks Bay 0102 | 2024-08-27 08:34 | 45531.3569 | 2024-08-27 10:44 | 45531.4472 | 0.18969 | 0.0014591 | 38 | 2479.9804 | Planned | Planned | Pole Replacements - Helicopter unable to fly due to wind
569 |  | 3139 | Nuhaka Opoutama Rd Waikokopu Rd Whaanga St Wai Station Rd | Wairoa | Nuhaka 3203 | 2024-08-27 09:04 | 45531.3778 | 2024-08-27 13:19 | 45531.5549 | 0.2252 | 0.00088315 | 23 | 2935.8516 | Planned | Planned | Replace Poles
570 |  | 3167 | Parkers Lane | Gisborne | Campion 0802 | 2024-08-27 09:04 | 45531.3778 | 2024-08-27 16:00 | 45531.6667 | 0.17571 | 0.00042238 | 11 | 4576 | Planned | Planned | Replace 11kV poles
571 |  | 3147 | Tyndall Rd Lawrence St Halley St | Gisborne | Herschell 0501 | 2024-08-27 09:05 | 45531.3785 | 2024-08-27 14:38 | 45531.6097 | 0.9462 | 0.0028415 | 74 | 12356.0096 | Planned | Planned | Replace and upgrade TX A289
572 |  | 3124 | Tapuihikitia Rd Rangatira Rd | Gisborne | Whatatutu 1201 | 2024-08-27 09:07 | 45531.3799 | 2024-08-27 12:34 | 45531.5236 | 0.087432 | 0.00042238 | 11 | 1138.9809 | Planned | Planned | Upgrade TX & DDO Fuses F442
573 |  | 29353 | Mahia Peninsula | Wairoa | Mahia 3301 | 2024-08-27 09:49 | 45531.409 | 2024-08-27 13:09 | 45531.5479 | 3.0975 | 0.072035 | 1876 | 80668 | Unplanned | Defective Equipment | Generator not running correctly. Speed Freq mismatch. Low oil pressure claims
574 |  | 29347 | Cobden Street | Gisborne | City 0602 | 2024-08-27 10:41 | 45531.4451 | 2024-09-05 06:26 | 45540.2681 | 0.14061 | 0.0072956 | 190 | 3662 | Unplanned | Defective Equipment | Cable termination failure @RMU B889. Fault at Library (old) open point B608
575 |  | 6688 | 243 Tuparoa Road | Gisborne | Ruatoria 0201 | 2024-08-27 17:50 | 45531.7431 | 2024-08-27 18:25 | 45531.7674 | 0.026879 | 0.00076796 | 20 | 700 | Unplanned | Adverse Weather | High winds
576 |  | 3145 | Taumata Road | Gisborne | Tahora 1103 | 2024-08-28 09:00 | 45532.375 | 2024-08-28 12:10 | 45532.5069 | 0.1605 | 0.00084476 | 22 | 2092.2302 | Planned | Planned | To install sectionaliser control @ switch D3416
577 |  | N/A 33 | Bell Road | Gisborne | Bell 1406 | 2024-08-29 00:15 | 45533.0104 | 2024-08-29 02:33 | 45533.1062 | 0.97999 | 0.0091003 | 237 | 25522 | Unplanned | Unknown cause | Patrol no fault found. No wind/rain
578 |  | 3141 | Nuhaka Opoutama Rd Waikokopu Rd Whaanga St Wai Station Rd | Wairoa | Nuhaka 3203 | 2024-08-29 09:03 | 45533.3771 | 2024-08-29 13:53 | 45533.5785 | 0.25611 | 0.00088315 | 23 | 3338.3516 | Planned | Planned | Replace 11kV poles
579 |  | 3151 | Rangitukia Rd Beach Rd East Cape Rd | Gisborne | Tiki Tiki 0206 | 2024-08-29 09:05 | 45533.3785 | 2024-08-29 15:32 | 45533.6472 | 0.69842 | 0.0018047 | 47 | 9110.9129 | Planned | Planned | Replace Poles
580 |  | 3152 | River Parade Bridge St Freyberg St | Wairoa | Borough One 3204 | 2024-08-29 09:06 | 45533.3792 | 2024-08-29 15:35 | 45533.6493 | 0.19418 | 0.00049917 | 13 | 2497.2459 | Planned | Planned | Upgrade TX W1534
581 |  | 29373 | East Cape Road | Gisborne | Te Araroa 0103 | 2024-08-29 11:41 | 45533.4868 | 2024-08-30 09:59 | 45534.416 | 0.4766 | 0.0013823 | 36 | 12412 | Unplanned | Defective Equipment | Replace x-arm @ pole J3764
582 |  | 29372 | Bushmere Road | Gisborne | Bell 1406 | 2024-08-29 14:32 | 45533.6056 | 2024-08-29 15:07 | 45533.6299 | 0.0040318 | 0.00011519 | 3 | 105 | Unplanned | Defective Equipment | To repair HV termination dead-end @ C5365
583 |  | 3157 | Kotare Road | Wairoa | Frasertown 3103 | 2024-08-30 09:14 | 45534.3847 | 2024-08-30 13:18 | 45534.5542 | 0.018738 | 7.6796e-05 | 2 | 244.0253 | Planned | Planned | Replace 11kV poles
584 |  | 7423 | 740 HereHeretu Road | Wairoa | Nuhaka 3203 | 2024-08-30 12:56 | 45534.5389 | 2024-08-30 14:00 | 45534.5833 | 0.0024575 | 3.8398e-05 | 1 | 64 | Unplanned | Vegetation | Replaced fuses
585 |  | 5575 | Waitangi Road | Gisborne | Kanakanaia 1202 | 2024-08-30 18:30 | 45534.7708 | 2024-08-30 20:30 | 45534.8542 | 0.059901 | 0.00049917 | 13 | 1560 | Unplanned | Unknown cause | Fuse fault
586 |  | 5577 | 1542 Panikau Road | Gisborne | Dalton 0502 | 2024-08-31 11:30 | 45535.4792 | 2024-08-31 12:38 | 45535.5264 | 0.0026111 | 3.8398e-05 | 1 | 68 | Unplanned | Unknown cause | Fuse fault
587 |  | N/A 35 | Waikura Valley Road | Gisborne | Hicks Bay 0102 | 2024-09-01 02:30 | 45536.1042 | 2024-09-01 11:24 | 45536.475 | 0.77917 | 0.0038782 | 101 | 20292 | Unplanned | Adverse Weather | No obvious fault found. High wind through area at the time
588 |  | 6690 | 1904 Waikura Road | Gisborne | Hicks Bay 0102 | 2024-09-01 07:10 | 45536.2986 | 2024-09-01 11:15 | 45536.4688 | 0.36689 | 0.0014975 | 39 | 9555 | Unplanned | Adverse Weather | Very wndy overnight through to 10:30am
589 |  | 29381 | Matawai Rd, Te Wera Rd, Koranga Valley Road | Gisborne | Matawai 1204 | 2024-09-01 12:29 | 45536.5201 | 2024-09-01 18:12 | 45536.7583 | 0.93511 | 0.0027263 | 71 | 24353 | Unplanned | Vegetation | High wind caused conductor to be caught in tree by Pole F1947
590 |  | 29383 | Stanley Road | Gisborne | Lytton 0701 | 2024-09-01 19:43 | 45536.8215 | 2024-09-03 17:50 | 45538.7431 | 0.04865 | 0.0029566 | 77 | 1267 | Unplanned | Defective Equipment | Blown 11kV cable termination
591 |  | 29388 | Awapuni Road | Gisborne | Awapuni 0606 | 2024-09-02 09:30 | 45537.3958 | 2024-09-05 14:24 | 45540.6 | 0.0055293 | 7.6796e-05 | 2 | 144 | Unplanned | Defective Equipment | Cable fault between fues switch B220 & TX B323
592 |  | 29394 | Waimata feeder, Ingram Rd | Gisborne | Waimata 0903 | 2024-09-02 17:52 | 45537.7444 | 2024-09-02 19:45 | 45537.8229 | 0.94778 | 0.02492 | 649 | 24683 | Unplanned | Defective Equipment | Wire down between pole D4547 & D4548. Broke Mid-span. No obvious cause
593 |  | 3179 | Cave Road | Gisborne | Whangara 0506 | 2024-09-03 08:32 | 45538.3556 | 2024-09-03 14:18 | 45538.5958 | 0.053143 | 0.00015359 | 4 | 1384 | Planned | Planned | Replace 11kV poles
594 |  | 3168 | Lake Road | Wairoa | Frasertown 3103 | 2024-09-03 09:00 | 45538.375 | 2024-09-03 16:19 | 45538.6799 | 1.9048 | 0.004339 | 113 | 49607 | Planned | Planned | Replace 50kV/11kV poles & Switchgear
595 |  | 3158 | Waiapu Road | Gisborne | Toko Tie 0401 | 2024-09-03 09:09 | 45538.3812 | 2024-09-03 16:31 | 45538.6882 | 0.69585 | 0.0015743 | 41 | 9054.7326 | Planned | Planned | Replace 11kV Poles
596 |  | 3159 | Lake Road | Wairoa | Frasertown 3103 | 2024-09-04 09:01 | 45539.3757 | 2024-09-04 15:55 | 45539.6632 | 0.22256 | 0.00053757 | 14 | 2899.5579 | Planned | Planned | Replace 11kV pole & TX W1693
597 |  | 29453 | Waimata Feeder | Gisborne | Waimata 0903 | 2024-09-05 07:42 | 45540.3208 | 2024-09-05 08:50 | 45540.3681 | 0.48474 | 0.02492 | 649 | 12624 | Unplanned | Third Party Interference | Bulk carrier dropped load at site and contacted OH 11kV
598 |  | 3180 | Cave Road | Gisborne | Whangara 0506 | 2024-09-05 08:31 | 45540.3549 | 2024-09-05 12:53 | 45540.5368 | 0.040241 | 0.00015359 | 4 | 1048 | Planned | Planned | Replace Poles
599 |  | 3160 | Waiapu Road | Gisborne | Toko Tie 0401 | 2024-09-05 09:00 | 45540.375 | 2024-09-05 16:11 | 45540.6743 | 0.67853 | 0.0015743 | 41 | 8849.4099 | Planned | Planned | Replace 11kV poles
600 |  | 29455 | Royd Rd | Gisborne | Waimata 0903 | 2024-09-05 09:34 | 45540.3986 | 2024-09-05 10:21 | 45540.4313 | 0.070384 | 0.0014975 | 39 | 1833 | Unplanned | Defective Equipment | Broken shackle insulator at Pole C2030
601 |  | 3161 | Waiapu Road | Gisborne | Toko Tie 0401 | 2024-09-06 09:00 | 45541.375 | 2024-09-06 13:17 | 45541.5535 | 0.26644 | 0.0010367 | 27 | 3474.1187 | Planned | Planned | Pole Replacement
602 |  | 3155 | Collin Street | Wairoa | Brickworks 3201 | 2024-09-06 09:02 | 45541.3764 | 2024-09-06 16:09 | 45541.6729 | 1.0985 | 0.0025727 | 67 | 14341.3007 | Planned | Planned | Replace TX W1576
603 |  | 29431 | Kipling Road | Gisborne | Kanakanaia 1202 | 2024-09-06 14:38 | 45541.6097 | 2024-09-06 16:03 | 45541.6687 | 0.34854 | 0.0068732 | 179 | 9077 | Unplanned | Defective Equipment | Cable termination failure@ pole F3386. Jumpers removed cable isolated
604 |  | 3203 | Renner Road | Gisborne | Lavenham 0902 | 2024-09-09 10:02 | 45544.4181 | 2024-09-09 11:36 | 45544.4833 | 0.0072188 | 7.6796e-05 | 2 | 188 | Unplanned | Third Party Interference | Stopbank construction LV installation + LV lines removed @ TX D360 until further notice
605 |  | 3169 | Kanakania Road | Gisborne | Kanakanaia 1202 | 2024-09-10 08:30 | 45545.3542 | 2024-09-10 15:59 | 45545.666 | 0.4655 | 0.0010367 | 27 | 6067.7842 | Planned | Planned | Replace poles & install new HV fuses @ E1107
606 |  | 3162a | Russell Parade, Carroll St | Wairoa | Frasertown 3103 | 2024-09-10 08:45 | 45545.3646 | 2024-09-10 08:59 | 45545.3743 | 0.00053757 | 3.8398e-05 | 1 | 0 | Planned | Planned | Install RMU & upgrade poles
607 |  | 3146 | Woodgreen / Ebbett Road | Wairoa | Ruakituri 2003 | 2024-09-10 09:00 | 45545.375 | 2024-09-10 12:12 | 45545.5083 | 0.28015 | 0.0014591 | 38 | 3654.6536 | Planned | Planned | Upgrade controls sectionalizer W799
608 |  | 3162 | Russell Parade, Carroll St | Wairoa | Frasertown 3103 | 2024-09-10 09:04 | 45545.3778 | 2024-09-10 17:58 | 45545.7486 | 1.2905 | 0.0025727 | 67 | 14953.8356 | Planned | Planned | Install RMU & upgrade poles
609 |  | 3162b | Russell Parade, Carroll St | Wairoa | Frasertown 3103 | 2024-09-10 17:00 | 45545.7083 | 2024-09-10 17:14 | 45545.7181 | 0.00053757 | 3.8398e-05 | 1 | 7.0003 | Planned | Planned | Install RMU & upgrade poles
610 |  | 3162 | Russell Parade, Carroll St | Wairoa | Frasertown 3103 | 2024-09-10 17:31 | 45545.7299 | 2024-09-10 17:52 | 45545.7444 | 0.033061 | 0.0016895 | 44 | 861 | Unplanned | Human Error | Install RMU and Upgrade poles
611 |  | 29476 | Makaretu Road | Gisborne | Matawai 1204 | 2024-09-11 06:35 | 45546.2743 | 2024-09-11 14:23 | 45546.5993 | 0.50394 | 0.0023423 | 61 | 13124 | Unplanned | Defective Equipment | Pin off crossarm pole F761
612 |  | 3171 | Motu Road | Gisborne | Matawai 1204 | 2024-09-11 08:31 | 45546.3549 | 2024-09-11 16:14 | 45546.6764 | 0.088891 | 0.00019199 | 5 | 1122.7155 | Planned | Planned | Replace 11kV poles
613 |  | 3172 | Bloomfield Road | Gisborne | Bushmere 0805 | 2024-09-11 08:33 | 45546.3562 | 2024-09-11 10:47 | 45546.4493 | 0.010291 | 7.6796e-05 | 2 | 134.0103 | Planned | Planned | Replace LV Poles
614 |  | 3192 | Ormond Valley Road | Gisborne | Waimata 0903 | 2024-09-11 08:34 | 45546.3569 | 2024-09-11 11:40 | 45546.4861 | 0.23569 | 0.0012671 | 33 | 6138 | Planned | Planned | Cut trees from 11kV line
615 |  | 3170 | Kanakania Road | Gisborne | Kanakanaia 1202 | 2024-09-12 08:30 | 45547.3542 | 2024-09-12 15:24 | 45547.6417 | 0.42921 | 0.0010367 | 27 | 5594.7944 | Planned | Planned | Replace 11kV Poles
616 |  | 3204 | Russel Parade | Wairoa | Frasertown 3103 | 2024-09-12 09:03 | 45547.3771 | 2024-09-12 14:42 | 45547.6125 | 0.26034 | 0.00076796 | 20 | 6780 | Planned | Planned | OHUG conversion from DDO W1626 to Fuse switch W1318
617 |  | 3163 | Russell Parade Road | Wairoa | Frasertown 3103 | 2024-09-12 09:03 | 45547.3771 | 2024-09-12 10:04 | 45547.4194 | 0.1069 | 0.0018431 | 48 | 1345.2386 | Planned | Planned | Disconnect redundant 11kV OH Pole W1258 - W1626
618 |  | 29449 | Hereheretau Road | Wairoa | Nuhaka 3203 | 2024-09-12 15:41 | 45547.6535 | 2024-09-12 16:30 | 45547.6875 | 0.035749 | 0.00072956 | 19 | 931 | Unplanned | Defective Equipment | Repair broken 11kV jumper @ pole W8506
619 |  | 3174 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2024-09-13 08:34 | 45548.3569 | 2024-09-13 13:07 | 45548.5465 | 0.073379 | 0.00026879 | 7 | 955.8104 | Planned | Planned | Replace Poles
620 |  | 3176 | Haisman Rd, Tuckers Road | Gisborne | Haisman 0804 | 2024-09-13 09:00 | 45548.375 | 2024-09-13 18:48 | 45548.7833 | 1.4902 | 0.0025343 | 66 | 14887.6339 | Planned | Planned | Replace Pole C5729 hit by car
621 |  | 29434 | Kipling Road | Gisborne | Te Karaka 1203 | 2024-09-13 14:54 | 45548.6208 | 2024-09-13 15:16 | 45548.6361 | 0.021119 | 0.00095995 | 25 | 550 | Unplanned | Defective Equipment | Repair cable term fault
622 |  | 3177 | Goodwin Road | Gisborne | Whangara 0506 | 2024-09-14 09:03 | 45549.3771 | 2024-09-14 11:26 | 45549.4764 | 0.082364 | 0.00057597 | 15 | 1073.1177 | Planned | Planned | Install new TX
623 |  | 3175 | Matawai | Gisborne | Matawai 1204 | 2024-09-17 08:30 | 45552.3542 | 2024-09-17 09:41 | 45552.4035 | 0.6434 | 0.0090619 | 236 | 3572.0793 | Planned | Planned | To replace Pole F1559. Install Sectionalisers at F423
624 |  | 3183 | Matawai Road | Gisborne | Matawai 1204 | 2024-09-17 08:31 | 45552.3549 | 2024-09-17 12:40 | 45552.5278 | 0.62147 | 0.0024959 | 65 | 5864.6009 | Planned | Planned | Replace 11kV pole F1962. Early start time due to Major Matawai S/down on Otoko Hill started prior to this advertised outage time.
625 |  | 3175a | Matawai | Gisborne | Matawai 1204 | 2024-09-17 08:32 | 45552.3556 | 2024-09-17 17:00 | 45552.7083 | 0.039012 | 7.6796e-05 | 2 | 478.0367 | Planned | Planned | To replace Pole F1559. Install Sectionalisers at F423
626 |  | 29478 | 3709 Whangara Road | Gisborne | Rototahi 0403 | 2024-09-17 09:34 | 45552.3986 | 2024-09-17 10:08 | 45552.4222 | 0.0013055 | 3.8398e-05 | 1 | 34 | Unplanned | Defective Equipment | Replaced 11kV termination dedend @ TX A150
627 |  | 3182 | Matawai Road | Gisborne | Matawai 1204 | 2024-09-17 13:07 | 45552.5465 | 2024-09-17 14:39 | 45552.6104 | 0.010598 | 0.00011519 | 3 | 138.0159 | Planned | Planned | Replaced TX F237
628 |  | 3175b | Matawai | Gisborne | Matawai 1204 | 2024-09-17 16:03 | 45552.6687 | 2024-09-17 17:00 | 45552.7083 | 0.51653 | 0.0090619 | 236 | 3214.8713 | Planned | Planned | To replace Pole F1559. Install Sectionalisers at F423
629 |  | 8425 | 1405 Wharekopae Road | Gisborne | Lavenham 0902 | 2024-09-17 16:40 | 45552.6944 | 2024-09-18 12:32 | 45553.5222 | 0.04577 | 3.8398e-05 | 1 | 1192 | Unplanned | Lightning | Replaced fuses
630 |  | 29517 | Wairere Road | Gisborne | Tamarau 0503 | 2024-09-17 16:42 | 45552.6958 | 2024-09-18 16:20 | 45553.6806 | 0.28153 | 0.0036094 | 94 | 7332 | Unplanned | Lightning | Lightening blew up cable term. Install generator
631 |  | 8424 | 88 Campbell Road | Gisborne | Lavenham 0902 | 2024-09-18 07:41 | 45553.3201 | 2024-09-18 08:30 | 45553.3542 | 0.015052 | 0.00030718 | 8 | 392 | Unplanned | Lightning | Replace DDO
632 |  | 7514 | 2762 Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2024-09-18 08:04 | 45553.3361 | 2024-09-18 12:30 | 45553.5208 | 0.030642 | 0.00011519 | 3 | 798 | Unplanned | Unknown cause | Replace fuses
633 |  | 3184 | Bushmere Road | Gisborne | Bell 1406 | 2024-09-18 08:36 | 45553.3583 | 2024-09-18 16:03 | 45553.6687 | 0.08582 | 0.00019199 | 5 | 1117.7145 | Planned | Planned | Replace LV poles
634 |  | 3156 | Morere Road | Wairoa | Nuhaka 3203 | 2024-09-18 09:00 | 45553.375 | 2024-09-18 12:14 | 45553.5097 | 1.147 | 0.0062973 | 164 | 14997.9744 | Planned | Planned | Upgraded Switch W810 to Sectionaliser
635 |  | 3189 | Tolaga Bay | Gisborne | Toko Tie 0401 | 2024-09-18 09:00 | 45553.375 | 2024-09-18 16:30 | 45553.6875 | 0.19007 | 0.00042238 | 11 | 1650.6969 | Planned | Planned | Replace ABS
636 |  | 29481 | Wharekopae Road | Gisborne | Lavenham 0902 | 2024-09-18 12:21 | 45553.5146 | 2024-09-19 13:54 | 45554.5792 | 0.058864 | 3.8398e-05 | 1 | 1533 | Unplanned | Lightning | Replace TX D1914
637 |  | 29482 | Wharekopae Road | Gisborne | Lavenham 0902 | 2024-09-18 12:51 | 45553.5354 | 2024-09-19 11:47 | 45554.491 | 0.052836 | 3.8398e-05 | 1 | 1376 | Unplanned | Lightning | Replace TX D52
638 |  | 7516 | 551 Parikanapa Road | Gisborne | Parikanapa 1002 | 2024-09-18 14:00 | 45553.5833 | 2024-09-18 15:00 | 45553.625 | 0.0023039 | 3.8398e-05 | 1 | 60 | Unplanned | Lightning | Replaced TX fuses
639 |  | 7419 | 3141 Mahia Eastcoast Road | Wairoa | Mahia 3301 | 2024-09-18 14:45 | 45553.6146 | 2024-09-19 11:00 | 45554.4583 | 0.41988 | 0.00034558 | 9 | 10935 | Unplanned | Adverse Weather | Replaced fuses
640 |  | 8432 | 148 Campbell Rd | Gisborne | Lavenham 0902 | 2024-09-18 18:34 | 45553.7736 | 2024-09-18 19:40 | 45553.8194 | 0.0025343 | 3.8398e-05 | 1 | 66 | Unplanned | Lightning | Replace DDA fuse
641 |  | 3193 | Wheatstone Road | Gisborne | Dalton 0502 | 2024-09-19 08:32 | 45554.3556 | 2024-09-19 15:11 | 45554.6326 | 0.4443 | 0.0011135 | 29 | 5791.9424 | Planned | Planned | Replace 11kV poles
642 |  | 3191 | Rutherford Street | Wairoa | Borough Two 3205 | 2024-09-19 08:34 | 45554.3569 | 2024-09-19 15:47 | 45554.6576 | 0.81469 | 0.0018815 | 49 | 10628.4599 | Planned | Planned | Upgrade TX W1548
643 |  | 3195 | Taylors bay | Wairoa | Mahia 3301 | 2024-09-20 08:34 | 45555.3569 | 2024-09-20 13:24 | 45555.5583 | 0.5345 | 0.0018431 | 48 | 6975.9244 | Planned | Planned | Replace Poles
644 |  | 3220 | Tuckers Road, Haisman Rd | Gisborne | Haisman 0804 | 2024-09-20 09:00 | 45555.375 | 2024-09-20 15:45 | 45555.6562 | 1.0264 | 0.0025343 | 66 | 26730 | Planned | Planned | To complete installation of replacement 50kV/11kV Pole C5729
645 |  | 3194 | Parkers Lane | Gisborne | Campion 0802 | 2024-09-20 09:03 | 45555.3771 | 2024-09-20 13:28 | 45555.5611 | 0.11193 | 0.00042238 | 11 | 1458.2666 | Planned | Planned | Replace HV poles
646 |  | 3223 | Whangara Road | Gisborne | Dalton 0502 | 2024-09-20 09:04 | 45555.3778 | 2024-09-20 13:21 | 45555.5563 | 0.35526 | 0.0013823 | 36 | 9252 | Planned | Planned | Replace Pole A784
647 |  | 3197 | Kabul Street | Wairoa | Borough One 3204 | 2024-09-20 09:05 | 45555.3785 | 2024-09-20 14:05 | 45555.5868 | 0.57597 | 0.0019199 | 50 | 7515.8392 | Planned | Planned | Replave TX W1577
648 |  | 8440 | 1K up Kaiaua Road | Gisborne | Toko Tie 0401 | 2024-09-21 07:46 | 45556.3236 | 2024-09-21 12:06 | 45556.5042 | 0.0099835 | 3.8398e-05 | 1 | 260 | Unplanned | Unknown cause | Replace DDO fuses
649 |  | 29495 | Kaiaua Road | Gisborne | Toko Tie 0401 | 2024-09-21 12:22 | 45556.5153 | 2024-09-21 13:00 | 45556.5417 | 0.023346 | 0.00061437 | 16 | 608 | Unplanned | Defective Equipment | Floating wire cracked insulator at pole G727
650 |  | 9410 | 3406 Whakarau Road | Gisborne | Matawai 1204 | 2024-09-22 19:34 | 45557.8153 | 2024-09-22 21:00 | 45557.875 | 0.0066045 | 7.6796e-05 | 2 | 172 | Unplanned | Unknown cause | Replace fuse
651 |  | 9411 | 1542 Panikau Road | Gisborne | Dalton 0502 | 2024-09-23 08:00 | 45558.3333 | 2024-09-23 10:00 | 45558.4167 | 0.04147 | 0.00034558 | 9 | 1080 | Unplanned | Unknown cause | Replace fruse
652 |  | 3198 | McDonalds Road | Gisborne | JNL_A 1405 | 2024-09-23 08:35 | 45558.3576 | 2024-09-23 14:29 | 45558.6035 | 0.081557 | 0.00023039 | 6 | 1062.2447 | Planned | Planned | Replace HV Bus
653 |  | 9412 | 1532 Whakekopae Road | Gisborne | Lavenham 0902 | 2024-09-23 09:30 | 45558.3958 | 2024-09-23 14:32 | 45558.6056 | 0.011596 | 3.8398e-05 | 1 | 302 | Unplanned | Unknown cause | Replaced fuse
654 |  | 3185 | Waikura Valley Road | Gisborne | Hicks Bay 0102 | 2024-09-24 08:31 | 45559.3549 | 2024-09-24 15:56 | 45559.6639 | 0.64931 | 0.0014591 | 38 | 8467.3369 | Planned | Planned | Replace HV poles
655 |  | 8706 | 3406 Whakarau Road | Gisborne | Matawai 1204 | 2024-09-24 08:49 | 45559.3674 | 2024-09-24 12:30 | 45559.5208 | 0.008486 | 3.8398e-05 | 1 | 221 | Unplanned | Adverse Weather | Replaced DDO's
656 |  | 3188 | Pongaroa / Onenui | Wairoa | Mahia 3301 | 2024-09-24 09:02 | 45559.3764 | 2024-09-24 13:29 | 45559.5618 | 1.1585 | 0.004339 | 113 | 15150.9557 | Planned | Planned | Upgrade remote switch W1221 to Sectionaliser
657 |  | 3201 | Waiapu Road | Gisborne | Toko Tie 0401 | 2024-09-24 09:04 | 45559.3778 | 2024-09-24 12:45 | 45559.5312 | 0.35641 | 0.0016127 | 42 | 4651.1601 | Planned | Planned | Replace ABS G42
658 |  | 7428 | 1737 Ohuka Road | Wairoa | Ruakituri 2003 | 2024-09-24 11:20 | 45559.4722 | 2024-09-24 14:00 | 45559.5833 | 0.061437 | 0.00038398 | 10 | 1600 | Unplanned | Unknown cause | Replace Fuses
659 |  | 8705 | 81 Waiherere Road | Gisborne | Waimata 0903 | 2024-09-24 13:36 | 45559.5667 | 2024-09-24 15:30 | 45559.6458 | 0.01751 | 0.00015359 | 4 | 456 | Unplanned | Vegetation | Replaced DDO
660 |  | 8703 | 1542 Panikau Road | Gisborne | Dalton 0502 | 2024-09-24 16:47 | 45559.6993 | 2024-09-24 20:00 | 45559.8333 | 0.066697 | 0.00034558 | 9 | 1737 | Unplanned | Adverse Weather | Replace DDO
661 |  | 8704 | 119 Hill Side Road | Gisborne | Ngatapa 1102 | 2024-09-24 17:49 | 45559.7424 | 2024-09-24 18:30 | 45559.7708 | 0.0031486 | 7.6796e-05 | 2 | 82 | Unplanned | Adverse Weather | Replaced DDO's
662 |  | 3202 | Crawford Road / Wainui Rd | Gisborne | Crawford 1504 | 2024-09-25 08:32 | 45560.3556 | 2024-09-25 15:34 | 45560.6486 | 1.831 | 0.004339 | 113 | 23946.4542 | Planned | Planned | Replace RMU
663 |  | 3199 | McDonalds Road | Gisborne | JNL_A 1405 | 2024-09-25 08:34 | 45560.3569 | 2024-09-25 14:56 | 45560.6222 | 0.088008 | 0.00023039 | 6 | 1146.264 | Planned | Planned | Replace HV poles
664 |  | 3186 | Waikura Valley Road | Gisborne | Hicks Bay 0102 | 2024-09-26 08:33 | 45561.3562 | 2024-09-26 12:48 | 45561.5333 | 0.37208 | 0.0014591 | 38 | 4854.9804 | Planned | Planned | Replace Poles
665 |  | 3200 | McDonalds Road | Gisborne | JNL_A 1405 | 2024-09-27 08:37 | 45562.359 | 2024-09-27 12:37 | 45562.5257 | 0.055293 | 0.00023039 | 6 | 720.2281 | Planned | Planned | Replace poles
666 |  | 3206 | Waiapu Road | Gisborne | Toko Tie 0401 | 2024-09-27 09:01 | 45562.3757 | 2024-09-27 13:25 | 45562.559 | 0.41562 | 0.0015743 | 41 | 5422.6503 | Planned | Planned | Replace Poles
667 |  | 3190 | Campbell Street | Wairoa | Brickworks 3201 | 2024-09-27 09:04 | 45562.3778 | 2024-09-27 14:52 | 45562.6194 | 0.6414 | 0.0018431 | 48 | 8367.3936 | Planned | Planned | Replace TX
668 |  | 29538 | Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2024-09-27 10:43 | 45562.4465 | 2024-09-27 15:27 | 45562.6438 | 0.10559 | 0.00072956 | 19 | 2750 | Unplanned | Defective Equipment | Broken conductor at bind
669 |  | 8702 | 263 Kaiaua Road | Gisborne | Toko Tie 0401 | 2024-09-27 15:15 | 45562.6354 | 2024-09-27 16:45 | 45562.6979 | 0.0034558 | 3.8398e-05 | 1 | 90 | Unplanned | Defective Equipment | Replace broken ddo
670 |  | 8701 | Pitcher Road | Gisborne | Te Karaka 1203 | 2024-09-27 16:47 | 45562.6993 | 2024-09-27 20:00 | 45562.8333 | 0.051876 | 0.00026879 | 7 | 1351 | Unplanned | Wildlife | Replaced ddo fuses
671 |  | 7427 | 370 SH2 Wairoa | Wairoa | Nuhaka 3203 | 2024-09-27 19:09 | 45562.7979 | 2024-09-27 20:00 | 45562.8333 | 0.0058749 | 0.00011519 | 3 | 153 | Unplanned | Unknown cause | Replace Fuses
672 |  | 3210 | Matawai Road | Gisborne | Te Karaka 1203 | 2024-09-28 09:04 | 45563.3778 | 2024-09-28 11:11 | 45563.466 | 0.10728 | 0.00084476 | 22 | 1398.1801 | Planned | Planned | Install new TX E1841
673 |  | 3215 | Awapuni Road | Gisborne | Lytton 0701 | 2024-10-01 09:02 | 45566.3764 | 2024-10-01 11:26 | 45566.4764 | 0.10506 | 0.00072956 | 19 | 1368.998 | Planned | Planned | Replace ampact joints & check cable toms
674 |  | 1621 | Maungataniwha | Wairoa | Raupunga 3101 | 2024-10-01 15:04 | 45566.6278 | 2024-10-01 16:08 | 45566.6722 | 0.02588 | 0.00042238 | 11 | 674 | Unplanned | Vegetation | Restore 11kV conductor after plantation clearance. Remove generator
675 |  | 3224 | Kaimoe Road | Gisborne | Lavenham 0902 | 2024-10-02 08:33 | 45567.3562 | 2024-10-02 10:06 | 45567.4208 | 0.078562 | 0.00084476 | 22 | 1023.8642 | Planned | Planned | To install Line fault indicators @ D315
676 |  | 3221 | SH 2 Waihua | Wairoa | Raupunga 3101 | 2024-10-02 09:00 | 45567.375 | 2024-10-02 14:16 | 45567.5944 | 1.8706 | 0.0069116 | 180 | 24432.8682 | Planned | Planned | Replace poles
677 |  | 3213 | Makarika | Gisborne | Makarika 0204 | 2024-10-02 09:05 | 45567.3785 | 2024-10-02 12:31 | 45567.5215 | 0.17855 | 0.00088315 | 23 | 2326.6646 | Planned | Planned | Cut trees
678 |  | 1622 | Tolaga Bay Sub | Gisborne | Rototahi 0403 | 2024-10-03 04:32 | 45568.1889 | 2024-10-03 10:00 | 45568.4167 | 0.26541 | 0.016588 | 432 | 6912 | Unplanned | Defective Equipment | Centre bolt out of x-arm @pole A908. Blown jumper @ pole A1071
679 |  | 1622 | Tolaga Bay Sub | Gisborne | Town 0402 | 2024-10-03 04:32 | 45568.1889 | 2024-10-03 10:01 | 45568.4174 | 0.27551 | 0.015743 | 410 | 7175 | Unplanned | Defective Equipment | Centre bolt out of x-arm @pole A908. Blown jumper @ pole A1071
680 |  | 1622 | Tolaga Bay Sub | Gisborne | Toko Tie 0401 | 2024-10-03 04:32 | 45568.1889 | 2024-10-03 10:30 | 45568.4375 | 0.21541 | 0.0065277 | 170 | 5610 | Unplanned | Defective Equipment | Centre bolt out of x-arm @pole A908. Blown jumper @ pole A1071
681 |  | 1622 | Tolaga Bay Sub | Gisborne | Tauwhareparae 0404 | 2024-10-03 04:32 | 45568.1889 | 2024-10-03 11:22 | 45568.4736 | 0.4809 | 0.011212 | 292 | 12524 | Unplanned | Defective Equipment | Centre bolt out of x-arm @pole A908. Blown jumper @ pole A1071
682 |  | 8602 | 160 Hikuwai Road | Gisborne | Mata 0304 | 2024-10-03 09:01 | 45568.3757 | 2024-10-03 11:05 | 45568.4618 | 0.023807 | 0.00019199 | 5 | 620 | Unplanned | Unknown cause | Replace HV fuses
683 |  | 8603 | 84 Koia Road | Gisborne | Tiki Tiki 0206 | 2024-10-03 16:42 | 45568.6958 | 2024-10-03 18:45 | 45568.7812 | 0.033061 | 0.00026879 | 7 | 861 | Unplanned | Unknown cause | Replace HV fuses
684 |  | 29544 | Ihungia Road | Gisborne | Mata 0304 | 2024-10-03 19:38 | 45568.8181 | 2024-10-04 15:33 | 45569.6479 | 0.17375 | 0.00061437 | 16 | 4525 | Unplanned | Vegetation | 2 span down between Poles H635 - H633. Pine tree out of zone
685 |  | 8604 | 5422 Te Araroa Road | Gisborne | Awatere 0101 | 2024-10-04 07:41 | 45569.3201 | 2024-10-04 12:00 | 45569.5 | 0.01989 | 7.6796e-05 | 2 | 518 | Unplanned | Unknown cause | Replace HV fuses
686 |  | 7429 | 3141 Mahia Eastcoast Road | Wairoa | Mahia 3301 | 2024-10-04 08:00 | 45569.3333 | 2024-10-04 11:00 | 45569.4583 | 0.062205 | 0.00034558 | 9 | 1620 | Unplanned | Unknown cause | Replace fuses
687 |  | 3222 | SH2 Waihua, Mohaka | Wairoa | Raupunga 3101 | 2024-10-04 09:03 | 45569.3771 | 2024-10-04 15:52 | 45569.6611 | 2.7312 | 0.0067197 | 175 | 35655.7821 | Planned | Planned | Pole Replacements
688 |  | 3222 | SH2 Waihua Mohaka | Wairoa | Raupunga 3101 | 2024-10-04 09:04 | 45569.3778 | 2024-10-04 15:49 | 45569.659 | 0.077756 | 0.00019199 | 5 | 2025 | Unplanned | Human Error | Pole Replacements
689 |  | 29545 | Koia Road | Gisborne | Tiki Tiki 0206 | 2024-10-04 10:28 | 45569.4361 | 2024-10-04 10:56 | 45569.4556 | 0.0032254 | 0.00011519 | 3 | 84 | Unplanned | Defective Equipment | Moved centre phase connection @ TX J241 to outside phase. Was only AB connection on Koia Road, other 2 TX were AC connections. AC fuses only used @ HV fuses J2076. Centre phase left deenergised, to reduce risk of line clash during hight winds.
690 |  | 1623 | Wharf Rd, Main Rd, Monkhouse Uawa Parade | Gisborne | Rototahi 0403 | 2024-10-04 15:13 | 45569.634 | 2024-10-04 15:39 | 45569.6521 | 0.12679 | 0.0048766 | 127 | 3302 | Unplanned | Defective Equipment | Faulty HV DDO fuse @ TX G2909
691 |  | 29549 | Te Araroa Road | Gisborne | Awatere 0101 | 2024-10-04 16:28 | 45569.6861 | 2024-10-04 18:12 | 45569.7583 | 0.051722 | 0.00072956 | 19 | 1347 | Unplanned | Defective Equipment | Broken Jumper @ HV Pole J2414
692 |  | 9319 | Waihau Tap off line | Gisborne | Rototahi 0403 | 2024-10-05 08:07 | 45570.3382 | 2024-10-05 09:30 | 45570.3958 | 0.044619 | 0.00053757 | 14 | 1162 | Unplanned | Unknown cause | Replace fuses
693 |  | 9320 | Tauwhareparae Road | Gisborne | Tauwhareparae 0404 | 2024-10-05 09:37 | 45570.4007 | 2024-10-05 13:45 | 45570.5729 | 0.019045 | 7.6796e-05 | 2 | 496 | Unplanned | Unknown cause | Replace fuses
694 |  | 3217 | Ahimanu Road | Gisborne | Parikanapa 1002 | 2024-10-07 08:38 | 45572.3597 | 2024-10-07 15:38 | 45572.6514 | 0.1774 | 0.00042238 | 11 | 0 | Planned | Planned | Replace HV poles
695 |  | N/A 41 | SH35 Waiapu Road | Gisborne | Inland 0301 | 2024-10-07 16:04 | 45572.6694 | 2024-10-07 19:41 | 45572.8201 | 0.17832 | 0.0061437 | 160 | 4644 | Unplanned | Vegetation | HV Conductor wrapped between poles H2036 - H2038. Caused by tree
696 |  | 8126 | Panikau Road | Gisborne | Dalton 0502 | 2024-10-07 20:09 | 45572.8396 | 2024-10-07 21:26 | 45572.8931 | 0.02661 | 0.00034558 | 9 | 693 | Unplanned | Unknown cause | Replaced fuse
697 |  | 3232 | Opoutama, Mahanga | Wairoa | Mahia 3301 | 2024-10-08 09:01 | 45573.3757 | 2024-10-08 16:28 | 45573.6861 | 4.0687 | 0.0092923 | 242 | 53205.1034 | Planned | Planned | To replace & Upgrade s/gear - W958 & W789. Install poles
698 |  | 29578 | Raupunga / Kotemaori | Wairoa | Raupunga 3101 | 2024-10-08 09:34 | 45573.3986 | 2024-10-08 16:57 | 45573.7063 | 0.82203 | 0.013746 | 358 | 21408 | Unplanned | Vegetation | Tree through HV Line @ 745 Waihua Valley Road
699 |  | 3236 | Lahore Street | Wairoa | Borough One 3204 | 2024-10-08 12:47 | 45573.5326 | 2024-10-08 18:46 | 45573.7819 | 0.78574 | 0.0021887 | 57 | 8083.1529 | Planned | Planned | Replacing Link Box 11373
700 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Solander 0706 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 22:05 | 45573.9201 | 0.042507 | 0.0015743 | 41 | 1107 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
701 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Cedenco A 0704 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 22:05 | 45573.9201 | 0.0031102 | 0.00011519 | 3 | 81 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
702 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Innes 0705 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 22:05 | 45573.9201 | 0.033176 | 0.0012287 | 32 | 864 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
703 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Chalmers 0707 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 22:06 | 45573.9208 | 0.7655 | 0.027339 | 712 | 19936 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
704 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Lytton 0701 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 22:06 | 45573.9208 | 0.076335 | 0.0027263 | 71 | 1988 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
705 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Willows 0702 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 22:06 | 45573.9208 | 0.089237 | 0.003187 | 83 | 2324 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
706 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Elgin 0703 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 22:06 | 45573.9208 | 0.99021 | 0.035365 | 921 | 25788 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
707 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Campion 0802 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 22:35 | 45573.941 | 1.5912 | 0.027915 | 727 | 41439 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
708 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Bushmere 0805 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 22:33 | 45573.9396 | 0.38436 | 0.0069884 | 182 | 10010 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
709 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Nelson 0803 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 23:08 | 45573.9639 | 3.0549 | 0.033944 | 884 | 79560 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
710 |  | N/A 36 | Makaraka - Parkinson Substations | Gisborne | Haisman 0804 | 2024-10-08 21:38 | 45573.9014 | 2024-10-08 23:09 | 45573.9646 | 3.3824 | 0.037169 | 968 | 88088 | Unplanned | Wildlife | Possum on 50kV Pole B1813 - found on ground. No Possum guards on this pole or others in proximity
711 |  | 3226 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2024-10-09 08:30 | 45574.3542 | 2024-10-09 11:16 | 45574.4694 | 0.1721 | 0.0010367 | 27 | 2245.6187 | Planned | Planned | To replace poles - Too windy for Helicoptor operations
712 |  | 3218 | Ahimanu Road | Gisborne | Parikanapa 1002 | 2024-10-09 08:35 | 45574.3576 | 2024-10-09 16:04 | 45574.6694 | 0.18965 | 0.00042238 | 11 | 2470.5431 | Planned | Planned | Replace Poles
713 |  | 3233 | Waikokopu - Opoutama | Wairoa | Mahia 3301 | 2024-10-09 09:06 | 45574.3792 | 2024-10-09 14:25 | 45574.6007 | 0.5757 | 0.0018047 | 47 | 7510.4955 | Planned | Planned | Replace ABS & Ghoritt recloser - Recloser not working
714 |  | 8606 | 4314 Ihungia Road | Gisborne | Mata 0304 | 2024-10-09 14:39 | 45574.6104 | 2024-10-09 16:00 | 45574.6667 | 0.065315 | 0.00080636 | 21 | 1701 | Unplanned | Unknown cause | Replace HV fuse
715 |  | 3235 | Tarnbrane Road | Gisborne | Bell 1406 | 2024-10-10 09:07 | 45575.3799 | 2024-10-10 14:54 | 45575.6208 | 0.50632 | 0.0014591 | 38 | 6602.62 | Planned | Planned | Replace x-arm & connect new u/ground and TX
716 |  | 29583 | Wharerata Road | Gisborne | Muriwai 0905 | 2024-10-11 05:07 | 45576.2132 | 2024-10-11 11:43 | 45576.4882 | 0.8471 | 0.0099835 | 260 | 22061 | Unplanned | Vegetation | Tree through HV C3768 - C3769
717 |  | 3219 | Ahimanu Road | Gisborne | Parikanapa 1002 | 2024-10-11 08:32 | 45576.3556 | 2024-10-11 12:16 | 45576.5111 | 0.094613 | 0.00042238 | 11 | 1232.8363 | Planned | Planned | Replace Poles
718 |  | 3243A | Piripaua Road | Wairoa | Frasertown 3103 | 2024-10-11 08:33 | 45576.3562 | 2024-10-11 14:14 | 45576.5931 | 0.18331 | 0.00053757 | 14 | 4774 | Planned | Planned | Tree Cutting
719 |  | 3225 | Waiapu Road | Gisborne | Makarika 0204 | 2024-10-11 09:02 | 45576.3764 | 2024-10-11 10:19 | 45576.4299 | 0.05322 | 0.00069116 | 18 | 694.8661 | Planned | Planned | To remove tree in close proximity
720 |  | 3239 | Rangiahua Road | Wairoa | Frasertown 3103 | 2024-10-14 08:52 | 45579.3694 | 2024-10-14 13:47 | 45579.5743 | 1.1627 | 0.0040318 | 105 | 15209.6925 | Planned | Planned | Cut Trees
721 |  | 29588 | Waimata Valley Road | Gisborne | Waimata 0903 | 2024-10-15 00:18 | 45580.0125 | 2024-10-15 14:58 | 45580.6236 | 0.12767 | 0.00023039 | 6 | 3325 | Unplanned | Third Party Interference | G614 Poles cut down
722 |  | 3240a | Motu Road | Gisborne | Matawai 1204 | 2024-10-15 08:30 | 45580.3542 | 2024-10-16 14:21 | 45581.5979 | 0.031909 | 7.6796e-05 | 2 | 415.5161 | Planned | Planned | Build new HV Line
723 |  | 3241 | Lahore St / Clyde Road | Wairoa | Borough One 3204 | 2024-10-15 08:34 | 45580.3569 | 2024-10-15 15:51 | 45580.6604 | 1.691 | 0.0043774 | 114 | 22073.7145 | Planned | Planned | Replace Link Box 11365
724 |  | 3238 | Rotoparu Road | Wairoa | Frasertown 3103 | 2024-10-15 08:37 | 45580.359 | 2024-10-15 15:04 | 45580.6278 | 1.0699 | 0.0027647 | 72 | 13970.5172 | Planned | Planned | Cut trees between W6543 - W6544
725 |  | 3228 | Hikuwai Road | Gisborne | Mata 0304 | 2024-10-15 09:10 | 45580.3819 | 2024-10-15 16:18 | 45580.6792 | 0.082172 | 0.00019199 | 5 | 1070.2054 | Planned | Planned | Replace Poles
726 |  | 29591 | Fortesque / Weld Street | Wairoa | Mahia 3301 | 2024-10-15 14:31 | 45580.6049 | 2024-10-15 16:01 | 45580.6674 | 0.1486 | 0.0016511 | 43 | 3870 | Unplanned | Defective Equipment | Broken LV Conductor @ W3506
727 |  | 3240 | Motu Road | Gisborne | Matawai 1204 | 2024-10-15 16:30 | 45580.6875 | 2024-10-16 08:30 | 45581.3542 | 0.036862 | 3.8398e-05 | 1 | 960 | Unplanned | Human Error | Build new HV Line
728 |  | 29594 | Raupunga - Mohuka | Wairoa | Raupunga 3101 | 2024-10-15 16:47 | 45580.6993 | 2024-10-16 15:00 | 45581.625 | 3.8882 | 0.044158 | 1150 | 101261 | Unplanned | Adverse Environment | Slip had moved pole centre, span clashed and welded to outside. Forest harvested recently, no protection from high winds.320m SPA
729 |  | N/A 42 | Poroporo Valley Road | Gisborne | Tiki Tiki 0206 | 2024-10-16 09:12 | 45581.3833 | 2024-10-16 11:01 | 45581.459 | 0.05441 | 0.00049917 | 13 | 1417 | Unplanned | Vegetation | Tree against HV conductor @ pole J1415
730 |  | 1626 | Pongoroa | Wairoa | Mahia 3301 | 2024-10-17 09:00 | 45582.375 | 2024-10-17 13:32 | 45582.5639 | 1.1584 | 0.0043006 | 112 | 30168 | Planned | Planned | To replace broken d/ends. Replace larch poles. Install HV links W8995
731 |  | 3229 | Hikuwai Road | Gisborne | Mata 0304 | 2024-10-17 09:08 | 45582.3806 | 2024-10-17 15:05 | 45582.6285 | 0.06854 | 0.00019199 | 5 | 892.6714 | Planned | Planned | Replace Poles
732 |  | 3244 | Waiapu Road | Gisborne | Makarika 0204 | 2024-10-17 10:03 | 45582.4187 | 2024-10-17 12:41 | 45582.5285 | 0.27908 | 0.0017663 | 46 | 3386.0236 | Planned | Planned | Complete pipework ABS J622. Replace cable stand-offs
733 |  | 3246 | Back Ormond Road | Gisborne | Waimata 0903 | 2024-10-18 08:31 | 45583.3549 | 2024-10-18 12:39 | 45583.5271 | 0.97132 | 0.0039166 | 102 | 12713.9164 | Planned | Planned | Replace ABS D432
734 |  | 3248 | Derby Street | Gisborne | Aberdeen 0609 | 2024-10-18 09:01 | 45583.3757 | 2024-10-18 10:02 | 45583.4181 | 0.24594 | 0.0040318 | 105 | 3215.4118 | Planned | Planned | Replace crucifix stand-off @B4197
735 |  | 3230 | Hikuwai Road | Gisborne | Mata 0304 | 2024-10-18 09:11 | 45583.3826 | 2024-10-18 14:07 | 45583.5882 | 0.056829 | 0.00019199 | 5 | 740.1584 | Planned | Planned | Replace Pole
736 |  | 29598 | Hexton | Gisborne | Patutahi Sub 09 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.00049917 | 3.8398e-05 | 1 | 13 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
737 |  | 29598 | Hexton | Gisborne | Lavenham 0902 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.22413 | 0.017241 | 449 | 5837 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
738 |  | 29598 | Hexton | Gisborne | Waimata 0903 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.32396 | 0.02492 | 649 | 8437 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
739 |  | 29598 | Hexton | Gisborne | Muriwai 0905 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.20616 | 0.015858 | 413 | 5369 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
740 |  | 29598 | Hexton | Gisborne | Te Arai 0906 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.11681 | 0.0089851 | 234 | 3042 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
741 |  | 29598 | Hexton | Gisborne | Pehiri Sub 10 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.00049917 | 3.8398e-05 | 1 | 13 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
742 |  | 29598 | Hexton | Gisborne | W O Kuri 1001 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.023461 | 0.0018047 | 47 | 611 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
743 |  | 29598 | Hexton | Gisborne | Parikanapa 1002 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.014975 | 0.0011519 | 30 | 390 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
744 |  | 29598 | Hexton | Gisborne | Tiniroto 1003 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.062397 | 0.0047998 | 125 | 1625 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
745 |  | 29598 | Hexton | Gisborne | Tahunga 1004 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.02446 | 0.0018815 | 49 | 637 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
746 |  | 29598 | Hexton | Gisborne | Ngatapa Sub 11 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.00049917 | 3.8398e-05 | 1 | 13 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
747 |  | 29598 | Hexton | Gisborne | Totangi 1101 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.0069884 | 0.00053757 | 14 | 182 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
748 |  | 29598 | Hexton | Gisborne | Ngatapa 1102 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.034942 | 0.0026879 | 70 | 910 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
749 |  | 29598 | Hexton | Gisborne | Tahora 1103 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:43 | 45583.4465 | 0.075375 | 0.0057981 | 151 | 1963 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
750 |  | 29598 | Hexton | Gisborne | Puha Sub 12 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:44 | 45583.4472 | 0.00053757 | 3.8398e-05 | 1 | 14 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
751 |  | 29598 | Hexton | Gisborne | Whatatutu 1201 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:44 | 45583.4472 | 0.13117 | 0.0093691 | 244 | 3416 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
752 |  | 29598 | Hexton | Gisborne | Kanakanaia 1202 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:44 | 45583.4472 | 0.096225 | 0.0068732 | 179 | 2506 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
753 |  | 29598 | Hexton | Gisborne | Te Karaka 1203 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:44 | 45583.4472 | 0.097838 | 0.0069884 | 182 | 2548 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
754 |  | 29598 | Hexton | Gisborne | Matawai 1204 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:44 | 45583.4472 | 0.20697 | 0.014783 | 385 | 5390 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
755 |  | 29598 | Hexton | Gisborne | Dunstan 1403 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:45 | 45583.4479 | 0.0063357 | 0.00042238 | 11 | 165 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
756 |  | 29598 | Hexton | Gisborne | JNL_A 1405 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:45 | 45583.4479 | 0.011519 | 0.00076796 | 20 | 300 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
757 |  | 29598 | Hexton | Gisborne | Bell 1406 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:45 | 45583.4479 | 0.13651 | 0.0091003 | 237 | 3555 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
758 |  | 29598 | Hexton | Gisborne | Waipaoa 1408 | 2024-10-18 10:30 | 45583.4375 | 2024-10-18 10:45 | 45583.4479 | 0.0034558 | 0.00023039 | 6 | 90 | Unplanned | Third Party Interference | Person felled tree throu line Somerton Road
759 |  | 3247 | Childers Road | Gisborne | Childers 0605 | 2024-10-18 12:01 | 45583.5007 | 2024-10-18 13:00 | 45583.5417 | 0.32623 | 0.0055293 | 144 | 4271.4885 | Planned | Planned | Replace LA's on Cruxifix
760 |  | 3249 | Stanley Road | Gisborne | Anzac 0604 | 2024-10-20 08:07 | 45585.3382 | 2024-10-20 16:53 | 45585.7035 | 0.30189 | 0.00057597 | 15 | 3932.3814 | Planned | Planned | Replace Oil RMU to Gas RMU
761 |  | 3251A | Sheltons Road | Gisborne | Rototahi 0403 | 2024-10-21 08:34 | 45586.3569 | 2024-10-21 15:59 | 45586.666 | 0.27339 | 0.00061437 | 16 | 3562.1872 | Planned | Planned | Pole replacement
762 |  | 3250 | Kawatiri Road | Gisborne | Waimata 0903 | 2024-10-21 09:02 | 45586.3764 | 2024-10-21 13:25 | 45586.559 | 0.30296 | 0.0011519 | 30 | 3950.1837 | Planned | Planned | Replace ABS D636
763 |  | 3256 | Whakato Road | Gisborne | Muriwai 0905 | 2024-10-21 09:05 | 45586.3785 | 2024-10-21 09:26 | 45586.3931 | 0.030642 | 0.0014591 | 38 | 399.5822 | Planned | Planned | Tap Changer (External) in-operable
764 |  | 29631 | Pehiri Area | Gisborne | Tahunga 1004 | 2024-10-22 07:09 | 45587.2979 | 2024-10-22 11:03 | 45587.4604 | 0.80048 | 0.0096763 | 252 | 20847 | Unplanned | Defective Equipment | D672 CB blew-up Leading to Incomer CB D776 opening. Line Patrol from CB D672 to end of cct was undertaken - no obvious fault. Fault proved to PMR Type CB. CB D672 Isolated
765 |  | 3257 | Tiniroto Road | Gisborne | Lavenham 0902 | 2024-10-22 08:35 | 45587.3576 | 2024-10-22 10:03 | 45587.4187 | 0.03379 | 0.00038398 | 10 | 440.1728 | Planned | Planned | Install fault indicators @ Pole D1368
766 |  | 3255 | Clifton Lyall Road | Wairoa | Frasertown 3103 | 2024-10-22 08:51 | 45587.3688 | 2024-10-22 16:21 | 45587.6813 | 0.069116 | 0.00015359 | 4 | 900.1382 | Planned | Planned | Tree cutting
767 |  | 3254 | Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2024-10-22 09:01 | 45587.3757 | 2024-10-22 14:21 | 45587.5979 | 0.57751 | 0.0018047 | 47 | 7533.9955 | Planned | Planned | Replace poles
768 |  | 3252 | Sheltons road | Gisborne | Rototahi 0403 | 2024-10-23 08:36 | 45588.3583 | 2024-10-23 15:22 | 45588.6403 | 0.24943 | 0.00061437 | 16 | 3249.9955 | Planned | Planned | Replace poles
769 |  | 3258 | Kirkpatrick Road | Gisborne | Waimata 0903 | 2024-10-23 09:00 | 45588.375 | 2024-10-23 14:37 | 45588.609 | 0.41408 | 0.0012287 | 32 | 5398.6254 | Planned | Planned | Replace TX Structure
770 |  | 3259 | Centennial Marine Drive | Gisborne | JNL_A 1405 | 2024-10-24 08:33 | 45589.3562 | 2024-10-24 15:59 | 45589.666 | 0.10275 | 0.00023039 | 6 | 1338.3083 | Planned | Planned | Replace TX C453 & 400V poles
771 |  | 3260 | Scott Street | Gisborne | Chalmers 0707 | 2024-10-24 09:02 | 45589.3764 | 2024-10-24 10:34 | 45589.4403 | 0.26141 | 0.0028415 | 74 | 3413.6723 | Planned | Planned | Replace Stand-offs
772 |  | 3268 | Waihi Road | Wairoa | Frasertown 3103 | 2024-10-24 09:35 | 45589.3993 | 2024-10-24 12:25 | 45589.5174 | 0.16542 | 0.00099835 | 26 | 2155.8892 | Planned | Planned | Install new Pole
773 |  | 29638 | Bruce Road | Gisborne | Kanakanaia 1202 | 2024-10-24 18:47 | 45589.7826 | 2024-10-24 19:21 | 45589.8063 | 0.0078332 | 0.00023039 | 6 | 204 | Unplanned | Defective Equipment | Repair blown jumper @ TX E212
774 |  | 3253 | Sheltons Road | Gisborne | Rototahi 0403 | 2024-10-25 08:37 | 45590.359 | 2024-10-25 15:53 | 45590.6618 | 0.26786 | 0.00061437 | 16 | 3490.1429 | Planned | Planned | Replace Poles
775 |  | 3261 | Huxley Road | Gisborne | Dalton 0502 | 2024-10-26 09:01 | 45591.3757 | 2024-10-26 09:53 | 45591.4118 | 0.45924 | 0.0088315 | 230 | 6040.9377 | Planned | Planned | Install Line fault indicators @ Pole A4137
776 |  | N/A 37 | Waimata | Gisborne | Tahora 1103 | 2024-10-26 17:02 | 45591.7097 | 2024-10-26 20:09 | 45591.8396 | 0.22563 | 0.0017663 | 46 | 5876 | Unplanned | Vegetation | Tree branch on line, tree leaning into line D3450
777 |  | N/A 38 | Ihungia | Gisborne | Mata 0304 | 2024-10-28 10:00 | 45593.4167 | 2024-10-28 13:28 | 45593.5611 | 0.09684 | 0.00061437 | 16 | 2522 | Unplanned | Unknown cause | Line closed back in
778 |  | 76431 | 353 Ruakituri Road | Wairoa | Ruakituri 2003 | 2024-10-28 10:25 | 45593.434 | 2024-10-28 12:30 | 45593.5208 | 0.0095995 | 7.6796e-05 | 2 | 250 | Unplanned | Unknown cause | Replace fuse
779 |  | 9206 | 353 Ruakituri Road | Wairoa | Ruakituri 2003 | 2024-10-28 11:00 | 45593.4583 | 2024-10-28 12:15 | 45593.5104 | 0.0057597 | 7.6796e-05 | 2 | 150 | Unplanned | Wildlife | Replace HV TX fuse
780 |  | 3245 | Wharekopae Road | Gisborne | Tahora 1103 | 2024-10-29 08:30 | 45594.3542 | 2024-10-29 09:28 | 45594.3944 | 0.12287 | 0.0021503 | 56 | 840.9216 | Planned | Planned | Install Generator Truck 300kVA - for work in Ngatapa Sub
781 |  | 3264 | Panikau Road | Gisborne | Dalton 0502 | 2024-10-29 08:30 | 45594.3542 | 2024-10-29 15:14 | 45594.6347 | 0.44987 | 0.0011135 | 29 | 5864.5231 | Planned | Planned | Replace Poles
782 |  | 3266 | Horehore Road | Gisborne | Makarika 0204 | 2024-10-29 09:03 | 45594.3771 | 2024-10-29 13:36 | 45594.5667 | 0.062896 | 0.00023039 | 6 | 531.1223 | Planned | Planned | To Remove Trees
783 |  | 3272 | Opoutama / Mahanga | Wairoa | Mahia 3301 | 2024-10-29 09:17 | 45594.3868 | 2024-10-29 16:00 | 45594.6667 | 2.9566 | 0.0073724 | 192 | 38679.4269 | Planned | Planned | To install new sectionaliser W900. Replace recloser W958. Replace defect pole W9074
784 |  | N/A 43 | Tahora | Gisborne | Ngatapa Sub 11 | 2024-10-29 09:46 | 45594.4069 | 2024-10-29 10:00 | 45594.4167 | 0.032216 | 0.0023423 | 61 | 839 | Unplanned | Human Error | CB D13 Closed to Bus Earth. Switching error. Generator feeding D141 - EOL Hahunga feeding D3416
785 |  | 8611 | Waione Road | Gisborne | Awatere 0101 | 2024-10-29 12:47 | 45594.5326 | 2024-10-29 16:55 | 45594.7049 | 0.14284 | 0.00057597 | 15 | 3720 | Unplanned | Unknown cause | Replace HV fuses
786 |  | 77187 | 57 Waione Road | Gisborne | Awatere 0101 | 2024-10-29 12:47 | 45594.5326 | 2024-10-29 15:45 | 45594.6562 | 0.10252 | 0.00057597 | 15 | 2670 | Unplanned | Unknown cause | Replace fuses
787 |  | 29643 | Kabul Streeet | Wairoa | Borough One 3204 | 2024-10-29 17:10 | 45594.7153 | 2024-10-29 18:02 | 45594.7514 | 0.52313 | 0.01006 | 262 | 13624 | Unplanned | Defective Equipment | Replace termination arms & DDO @ Pole W1419
788 |  | 3262 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2024-10-30 08:30 | 45595.3542 | 2024-10-30 15:13 | 45595.634 | 0.41781 | 0.0010367 | 27 | 5446.1404 | Planned | Planned | Replace Poles
789 |  | 3263 | Barkers Hill Road | Gisborne | Aberdeen 0609 | 2024-10-30 09:04 | 45595.3778 | 2024-10-30 14:05 | 45595.5868 | 1.0633 | 0.0035326 | 92 | 13894.9126 | Planned | Planned | Build and connect a temporary 11kV O/Head circuit and remove redundant circuit. For hill reinstatement roadworkds
790 |  | N/A 39 | Mahia | Wairoa | Morere 3401 | 2024-10-30 15:28 | 45595.6444 | 2024-10-30 15:46 | 45595.6569 | 0.18523 | 0.010291 | 268 | 4824 | Unplanned | Lightning | Lightning in the area
791 |  | N/A 39 | Mahia | Wairoa | Mahia 3301 | 2024-10-30 15:28 | 45595.6444 | 2024-10-30 15:51 | 45595.6604 | 0.77917 | 0.036017 | 938 | 20292 | Unplanned | Lightning | Lightning in the area
792 |  | 77898 | 2507 Tiniroto Road | Wairoa | Ruakituri 2003 | 2024-10-30 18:49 | 45595.784 | 2024-10-30 20:00 | 45595.8333 | 0.0027263 | 3.8398e-05 | 1 | 71 | Unplanned | Unknown cause | Replace fuses
793 |  | 78039 | Panikau Road | Gisborne | Dalton 0502 | 2024-10-30 20:29 | 45595.8535 | 2024-10-30 23:00 | 45595.9583 | 0.052183 | 0.00034558 | 9 | 1359 | Unplanned | Unknown cause | Replace fuse
794 |  | 5582 | Panikau Road | Gisborne | Dalton 0502 | 2024-10-30 20:30 | 45595.8542 | 2024-10-30 22:00 | 45595.9167 | 0.031102 | 0.00034558 | 9 | 810 | Unplanned | Unknown cause | Replace fuse
795 |  | 3269 | Kaiti Mall | Gisborne | Wainui 0504 | 2024-10-30 21:02 | 45595.8764 | 2024-10-30 23:56 | 45595.9972 | 0.40088 | 0.0023039 | 60 | 5232.0263 | Planned | Planned | Upgrade 400V S/Board at TX A256
796 |  | 78238 | 2151 Tiniroto Road | Wairoa | Ruakituri 2003 | 2024-10-31 07:55 | 45596.3299 | 2024-10-31 08:55 | 45596.3715 | 0.0023039 | 3.8398e-05 | 1 | 60 | Unplanned | Unknown cause | Replace fuses
797 |  | 3265 | Panikau Road | Gisborne | Dalton 0502 | 2024-10-31 08:30 | 45596.3542 | 2024-10-31 15:29 | 45596.6451 | 0.46657 | 0.0011135 | 29 | 6082.2653 | Planned | Planned | Replace 11kV poles
798 |  | 3271 | 5416 Te Araroa Road | Gisborne | Hicks Bay 0102 | 2024-10-31 11:01 | 45596.459 | 2024-10-31 12:30 | 45596.5208 | 0.037592 | 0.00042238 | 11 | 489.9878 | Planned | Planned | Upgrade TX J286
799 |  | 3245A | Wharekopae Road | Gisborne | Tahora 1103 | 2024-10-31 16:01 | 45596.6674 | 2024-10-31 16:48 | 45596.7 | 0.10106 | 0.0021503 | 56 | 0 | Planned | Planned | Removing Generator Truck 300kVA after work in Ngatapa Sub
800 |  | 5584 | Arakini Road | Gisborne | Tauwhareparae 0404 | 2024-10-31 19:25 | 45596.809 | 2024-10-31 21:45 | 45596.9062 | 0.016127 | 0.00011519 | 3 | 420 | Unplanned | Unknown cause | Replace DDO fuse
801 |  | 78650 | 6 Hillcrest Road | Wairoa | Borough Two 3205 | 2024-10-31 20:05 | 45596.8368 | 2024-10-31 23:30 | 45596.9792 | 0.0078716 | 3.8398e-05 | 1 | 205 | Unplanned | Unknown cause | Replace fuse
802 |  | 3280 | Wharerata road | Gisborne | Muriwai 0905 | 2024-11-01 08:30 | 45597.3542 | 2024-11-01 13:29 | 45597.5618 | 0.26406 | 0.00088315 | 23 | 2417.1328 | Planned | Planned | Install new Pole & TX at C628
803 |  | 78847 | Bushy Knoll Cell Site | Gisborne | Tiniroto 1003 | 2024-11-01 12:13 | 45597.509 | 2024-11-01 15:30 | 45597.6458 | 0.015129 | 7.6796e-05 | 2 | 394 | Unplanned | Unknown cause | Replace fuses
804 |  | 8612 | 526 Tuparoa Road | Gisborne | Ruatoria 0201 | 2024-11-01 17:28 | 45597.7278 | 2024-11-01 19:10 | 45597.7986 | 0.0039166 | 3.8398e-05 | 1 | 102 | Unplanned | Unknown cause | Replace fuse
805 |  | 78981 | 526 Tuparoa Road | Gisborne | Ruatoria 0201 | 2024-11-01 17:28 | 45597.7278 | 2024-11-01 18:30 | 45597.7708 | 0.0023807 | 3.8398e-05 | 1 | 62 | Unplanned | Wildlife | Replace fusewire
806 |  | N/A 40 | Pehiri Sub & Ngatapa Sub | Gisborne | W O Kuri 1001 | 2024-11-02 06:51 | 45598.2854 | 2024-11-02 07:41 | 45598.3201 | 0.090235 | 0.0018047 | 47 | 2350 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN
807 |  | N/A 40 | Pehiri Sub & Ngatapa Sub | Gisborne | Parikanapa 1002 | 2024-11-02 06:51 | 45598.2854 | 2024-11-02 08:08 | 45598.3389 | 0.088699 | 0.0011519 | 30 | 2310 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN
808 |  | N/A 40 | Pehiri Sub & Ngatapa Sub | Gisborne | Tahunga 1004 | 2024-11-02 06:51 | 45598.2854 | 2024-11-02 08:08 | 45598.3389 | 0.14488 | 0.0018815 | 49 | 3773 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN
809 |  | N/A 40 | Pehiri Sub & Ngatapa Sub | Gisborne | Tiniroto 1003 | 2024-11-02 06:51 | 45598.2854 | 2024-11-02 08:09 | 45598.3396 | 0.37438 | 0.0047998 | 125 | 9750 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN
810 |  | N/A 40 | Pehiri Sub & Ngatapa Sub | Gisborne | Tahora 1103 | 2024-11-02 06:51 | 45598.2854 | 2024-11-02 09:02 | 45598.3764 | 0.67293 | 0.0057981 | 151 | 17525 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN
811 |  | N/A 40 | Pehiri Sub & Ngatapa Sub | Gisborne | Ngatapa 1102 | 2024-11-02 06:51 | 45598.2854 | 2024-11-02 08:50 | 45598.3681 | 0.31986 | 0.0026879 | 70 | 8330 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN
812 |  | N/A 40 | Pehiri Sub & Ngatapa Sub | Gisborne | Totangi 1101 | 2024-11-02 06:51 | 45598.2854 | 2024-11-02 09:02 | 45598.3764 | 0.070422 | 0.00053757 | 14 | 1834 | Unplanned | Unknown cause | 50Kv cb22 Tripped (EF). Supply restored via 11kV to Ngatapa and Pehiri sub feeders. 50kV circuits closed back IN
813 |  | 80087 | 1235 Panikau Road | Gisborne | Dalton 0502 | 2024-11-03 04:53 | 45599.2035 | 2024-11-03 09:00 | 45599.375 | 0.085359 | 0.00034558 | 9 | 2223 | Unplanned | Vegetation | Replace fuse
814 |  | 3274 | Queen Street | Wairoa | Borough Two 3205 | 2024-11-03 08:41 | 45599.3618 | 2024-11-03 15:28 | 45599.6444 | 0.43758 | 0.0010751 | 28 | 4470.8016 | Planned | Planned | Replace Link Boxes 11212 & 11201
815 |  | 79868 | 1857 Ruakaka Road | Gisborne | Tiniroto 1003 | 2024-11-03 16:49 | 45599.7007 | 2024-11-03 19:00 | 45599.7917 | 0.0050301 | 3.8398e-05 | 1 | 131 | Unplanned | Unknown cause | Replace fuse
816 |  | 29712 | Gladstone/Childers/Palmerston/Wellington/Stanley | Gisborne | Childers 0605 | 2024-11-04 10:45 | 45600.4479 | 2024-11-04 17:30 | 45600.7292 | 2.2912 | 0.076681 | 1997 | 59669 | Unplanned | Defective Equipment | RMU B6542/B6541/B6540/B6539 - Faulted during switching operation 3273 when breaking a parallel. Able to Isolate & restore all customers except Wellington Street. 300kVA generator installed @ TX B40. GGHS off for whole period.
817 |  | 3275 | Titirangi Road | Wairoa | Frasertown 3103 | 2024-11-05 08:35 | 45601.3576 | 2024-11-05 16:23 | 45601.6826 | 0.28752 | 0.00061437 | 16 | 3746.3002 | Planned | Planned | Isolation to cut trees
818 |  | 81949 | 757 Whakaangiangi Road | Gisborne | Awatere 0101 | 2024-11-06 05:44 | 45602.2389 | 2024-11-06 08:50 | 45602.3681 | 0.014284 | 7.6796e-05 | 2 | 372 | Unplanned | Unknown cause | Replace fuses
819 |  | 3277 | Kiore Road | Gisborne | Tauwhareparae 0404 | 2024-11-06 08:32 | 45602.3556 | 2024-11-06 15:36 | 45602.65 | 0.17909 | 0.00042238 | 11 | 2332.985 | Planned | Planned | Replace Poles
820 |  | 82018 | 2108 tiniroto Road | Wairoa | Ruakituri 2003 | 2024-11-06 08:58 | 45602.3736 | 2024-11-06 10:45 | 45602.4479 | 0.0041086 | 3.8398e-05 | 1 | 107 | Unplanned | Unknown cause | Replace fuses
821 |  | 3276 | Titirangi Road | Wairoa | Frasertown 3103 | 2024-11-07 08:36 | 45603.3583 | 2024-11-07 14:36 | 45603.6083 | 0.22117 | 0.00061437 | 16 | 2881.7694 | Planned | Planned | Cut Trees away for O/Head
822 |  | 3281 | Wharekiri Road | Gisborne | Dalton 0502 | 2024-11-07 09:01 | 45603.3757 | 2024-11-07 14:21 | 45603.5979 | 0.31947 | 0.00099835 | 26 | 8320 | Planned | Planned | Replace Poles
823 |  | 3278 | Kiore Road | Gisborne | Tauwhareparae 0404 | 2024-11-08 08:32 | 45604.3556 | 2024-11-08 14:33 | 45604.6062 | 0.15248 | 0.00042238 | 11 | 1986.3386 | Planned | Planned | Replace Poles
824 |  | 29690 | Matawai Road | Gisborne | Waimata 0903 | 2024-11-09 09:57 | 45605.4146 | 2024-11-09 12:34 | 45605.5236 | 0.11454 | 0.00072956 | 19 | 2983 | Unplanned | Third Party Interference | Car V's Pole D658
825 |  | 3273 | Cobden / Derby / Childers | Gisborne | City 0602 | 2024-11-09 21:18 | 45605.8875 | 2024-11-09 21:55 | 45605.9132 | 0.013478 | 0.00072956 | 19 | 258.0021 | Unplanned | Human Error | Error by controller. Started switching in wrong place
826 |  | 3287 | Bushmere Road | Gisborne | Bell 1406 | 2024-11-11 09:01 | 45607.3757 | 2024-11-11 10:25 | 45607.434 | 0.041931 | 0.00049917 | 13 | 546.3894 | Planned | Planned | Install 11kV/400V line brakes at pole C5340 / C5342
827 |  | 3279 | Kiore Road | Gisborne | Tauwhareparae 0404 | 2024-11-12 08:38 | 45608.3597 | 2024-11-12 15:57 | 45608.6646 | 0.18542 | 0.00042238 | 11 | 2415.5198 | Planned | Planned | Replace Poles
828 |  | 3282 | Waihi Road | Wairoa | Frasertown 3103 | 2024-11-12 09:04 | 45608.3778 | 2024-11-12 17:40 | 45608.7361 | 0.35664 | 0.00069116 | 18 | 3746.5877 | Planned | Planned | Replace Poles
829 |  | 29691 | Bloomfield Road | Gisborne | Bell 1406 | 2024-11-12 10:29 | 45608.4368 | 2024-11-12 15:41 | 45608.6535 | 0.046654 | 0.0011519 | 30 | 1215 | Unplanned | Human Error | To install & Remove 11kV line breat @ Pole C5270. Overlooked when prepping switching for 110kV
830 |  | 86025 | 352 Mahaki Settlement Rd | Gisborne | Matawai 1204 | 2024-11-12 18:01 | 45608.7507 | 2024-11-12 20:50 | 45608.8681 | 0.051914 | 0.00030718 | 8 | 1352 | Unplanned | Defective Equipment | Re-fixed crossarm to pole, re-livened
831 |  | 86294 | 1235 Panikau Road | Gisborne | Dalton 0502 | 2024-11-13 03:54 | 45609.1625 | 2024-11-13 14:22 | 45609.5986 | 0.21703 | 0.00034558 | 9 | 5652 | Unplanned | Unknown cause | Replace fuse
832 |  | 86317 | Tutamoe Stn, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2024-11-13 06:07 | 45609.2549 | 2024-11-13 10:00 | 45609.4167 | 0.098414 | 0.00042238 | 11 | 2563 | Unplanned | Unknown cause | Replace fuse
833 |  | 3293 | Awapuni Road | Gisborne | Willows 0702 | 2024-11-13 09:02 | 45609.3764 | 2024-11-13 10:15 | 45609.4271 | 0.019621 | 0.00026879 | 7 | 255.5687 | Planned | Planned | To replace defected Ampacts
834 |  | 3283 | Ramotu Road | Wairoa | Frasertown 3103 | 2024-11-13 09:12 | 45609.3833 | 2024-11-13 14:02 | 45609.5847 | 0.11135 | 0.00038398 | 10 | 1440.5529 | Planned | Planned | Install new TX W4271
835 |  | 3290 | Kiore Road | Gisborne | Tauwhareparae 0404 | 2024-11-14 08:31 | 45610.3549 | 2024-11-14 15:06 | 45610.6292 | 0.12134 | 0.00030718 | 8 | 1580.4854 | Planned | Planned | Replace poles
836 |  | 3289 | Bushmere Road | Gisborne | Bell 1406 | 2024-11-14 09:01 | 45610.3757 | 2024-11-14 10:37 | 45610.4424 | 0.047921 | 0.00049917 | 13 | 624.3894 | Planned | Planned | Rejoin 11kV lin breaks @ Pole C5340 & C5342
837 |  | 3292 | Waihi Road | Wairoa | Frasertown 3103 | 2024-11-14 09:13 | 45610.384 | 2024-11-14 16:44 | 45610.6972 | 0.17318 | 0.00038398 | 10 | 2035.7814 | Planned | Planned | Replace Poles
838 |  | 29733 | Mahia | Wairoa | Mahia 3301 | 2024-11-14 09:18 | 45610.3875 | 2024-11-14 17:10 | 45610.7153 | 1.8585 | 0.0086012 | 224 | 48401 | Unplanned | Defective Equipment | Burnt-outx-arm. Failed Insulator
839 |  | 3295 | Taumata Road | Gisborne | Tahora 1103 | 2024-11-15 08:30 | 45611.3542 | 2024-11-15 15:52 | 45611.6611 | 0.37165 | 0.00084476 | 22 | 4842.1603 | Planned | Planned | Replace 11kV poles
840 |  | 3291 | Kiore Road | Gisborne | Tauwhareparae 0404 | 2024-11-15 08:35 | 45611.3576 | 2024-11-15 11:30 | 45611.4792 | 0.013439 | 7.6796e-05 | 2 | 175.0253 | Planned | Planned | Replaced LV poles beyond TX G144
841 |  | 3294 | Waihi Road | Wairoa | Frasertown 3103 | 2024-11-15 09:03 | 45611.3771 | 2024-11-15 14:50 | 45611.6181 | 0.13324 | 0.00038398 | 10 | 1735.6662 | Planned | Planned | Replace 11kv Pole
842 |  | 3288 | Anzac St / Kahutia Street | Gisborne | Anzac 0604 | 2024-11-15 17:15 | 45611.7188 | 2024-11-15 17:38 | 45611.7347 | 0.11807 | 0.0054141 | 141 | 1060.4677 | Planned | Planned | Phase out @ Gas switch B751
843 |  | 3320 | Childers Road | Gisborne | Childers 0605 | 2024-11-15 21:17 | 45611.8868 | 2024-11-15 21:41 | 45611.9035 | 0.048842 | 0.0020351 | 53 | 1272 | Planned | Planned | Phase out of Childers feeder cable - Urgent Work
844 |  | 88272 | 927 Koranga Valley road | Gisborne | Matawai 1204 | 2024-11-16 07:54 | 45612.3292 | 2024-11-16 13:15 | 45612.5521 | 0.012326 | 3.8398e-05 | 1 | 321 | Unplanned | Unknown cause | Replace fuse
845 |  | 88294 | 121 Maraehare Riad | Gisborne | Awatere 0101 | 2024-11-16 08:23 | 45612.3493 | 2024-11-16 10:45 | 45612.4479 | 0.027263 | 0.00019199 | 5 | 710 | Unplanned | Unknown cause | Replace fuse
846 |  | 3299 | Gladstone Road | Gisborne | Campion 0802 | 2024-11-16 09:01 | 45612.3757 | 2024-11-16 13:59 | 45612.5826 | 0.51492 | 0.0017279 | 45 | 6716.6634 | Planned | Planned | Replace TX C433
847 |  | 3296 | Taumata Road | Gisborne | Tahora 1103 | 2024-11-18 08:30 | 45614.3542 | 2024-11-18 16:30 | 45614.6875 | 0.40433 | 0.00084476 | 22 | 4945.2114 | Planned | Planned | Replace 11kV poles
848 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Ngatapa Sub 11 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 13:29 | 45614.5618 | 0.00015359 | 3.8398e-05 | 1 | 4 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
849 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Totangi 1101 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 13:29 | 45614.5618 | 0.0021503 | 0.00053757 | 14 | 56 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
850 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Ngatapa 1102 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 13:29 | 45614.5618 | 0.010751 | 0.0026879 | 70 | 280 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
851 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Tahora 1103 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 13:29 | 45614.5618 | 0.023192 | 0.0057981 | 151 | 604 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
852 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Pehiri Sub 10 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 13:29 | 45614.5618 | 0.00015359 | 3.8398e-05 | 1 | 4 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
853 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | W O Kuri 1001 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 13:29 | 45614.5618 | 0.0072188 | 0.0018047 | 47 | 188 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
854 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Parikanapa 1002 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 13:29 | 45614.5618 | 0.0046078 | 0.0011519 | 30 | 120 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
855 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Tiniroto 1003 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 13:29 | 45614.5618 | 0.019199 | 0.0047998 | 125 | 500 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
856 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Tahunga 1004 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 13:29 | 45614.5618 | 0.007526 | 0.0018815 | 49 | 196 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
857 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Lavenham 0902 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 14:02 | 45614.5847 | 0.57497 | 0.017241 | 449 | 14974 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
858 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Waimata 0903 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 14:02 | 45614.5847 | 0.92205 | 0.02492 | 649 | 24013 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
859 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Te Arai 0906 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 14:02 | 45614.5847 | 0.33245 | 0.0089851 | 234 | 8658 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
860 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Puha Sub 12 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 14:02 | 45614.5847 | 0.0014207 | 3.8398e-05 | 1 | 37 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
861 |  | 29746 | Patutahi/Pehiri/Ngatapa Subs | Gisborne | Muriwai 0905 | 2024-11-18 13:25 | 45614.559 | 2024-11-18 14:15 | 45614.5938 | 0.79292 | 0.015858 | 413 | 20650 | Unplanned | Third Party Interference | 50Kv Pole C3016 broke 1/2 way up (Potential Tractor strike). CB D644 Muriwai fail to close
862 |  | 90289 | 362 Whakaangiangi Rd | Gisborne | Awatere 0101 | 2024-11-19 09:12 | 45615.3833 | 2024-11-19 11:10 | 45615.4653 | 0.004531 | 3.8398e-05 | 1 | 118 | Unplanned | Unknown cause | Replace fuse
863 |  | N/A 44 | Te Reinga / Mahurangi / Whakapunaki | Wairoa | Ruakituri 2003 | 2024-11-19 14:29 | 45615.6035 | 2024-11-19 17:04 | 45615.7111 | 0.18393 | 0.0013055 | 34 | 4790 | Unplanned | Defective Equipment | Faulty lightning arrestor @ TX W1778
864 |  | 29751 | Waiapu Road | Gisborne | Inland 0301 | 2024-11-20 04:36 | 45616.1917 | 2024-11-21 11:45 | 45617.4896 | 0.60918 | 0.0061437 | 160 | 15865 | Unplanned | Wildlife | Suspect bird strike - Conductor down across river
865 |  | 3302 | Stout Street | Gisborne | Aberdeen 0609 | 2024-11-20 07:20 | 45616.3056 | 2024-11-20 07:34 | 45616.3153 | 0.03763 | 0.0026879 | 70 | 350.9408 | Planned | Planned | Replace Oil RMU to Gas CFC RMU
866 |  | 3304 | Wheatstone Road | Gisborne | Dalton 0502 | 2024-11-20 08:32 | 45616.3556 | 2024-11-20 14:24 | 45616.6 | 0.39197 | 0.0011135 | 29 | 5109.8127 | Planned | Planned | Replace HV Poles
867 |  | 3297 | Taumata Road | Gisborne | Tahora 1103 | 2024-11-20 08:34 | 45616.3569 | 2024-11-20 15:32 | 45616.6472 | 0.48151 | 0.0011519 | 30 | 6277.2227 | Planned | Planned | Replace poles
868 |  | 29750 | Waiomatatini Road | Gisborne | Tiki Tiki 0206 | 2024-11-20 12:27 | 45616.5188 | 2024-11-20 13:52 | 45616.5778 | 0.055485 | 0.00065277 | 17 | 1445 | Unplanned | Third Party Interference | Repaired broken conductor between poles J2904 & J2905. Digger contact on conductor
869 |  | 29755 | Te Hau Road | Gisborne | Whatatutu 1201 | 2024-11-20 16:10 | 45616.6736 | 2024-11-20 18:48 | 45616.7833 | 0.091003 | 0.00057597 | 15 | 2370 | Unplanned | Third Party Interference | Digger came in contact with HV line @ pole E1976 - E1977
870 |  | 90912 | 110 Te Hau Rd, Whatatutu | Gisborne | Whatatutu 1201 | 2024-11-20 16:10 | 45616.6736 | 2024-11-20 18:20 | 45616.7639 | 0.11481 | 0.00088315 | 23 | 2990 | Unplanned | Human Error | 0
871 |  | 3302 A | Stout Street | Gisborne | Aberdeen 0609 | 2024-11-20 17:17 | 45616.7201 | 2024-11-20 17:34 | 45616.7319 | 0.045694 | 0.0026879 | 70 | 456.223 | Planned | Planned | Replace Oil RMU to Gas CFC RMU
872 |  | 3338 | Hicks Bay / Lottin Point / Waikura Valley | Gisborne | Hicks Bay 0102 | 2024-11-21 09:00 | 45617.375 | 2024-11-21 13:57 | 45617.5813 | 1.0378 | 0.0034942 | 91 | 27027 | Planned | Planned | To replace pole J4074 - Urgent Work
873 |  | 3298 | Waihi Road | Wairoa | Frasertown 3103 | 2024-11-21 09:02 | 45617.3764 | 2024-11-21 15:49 | 45617.659 | 0.15628 | 0.00038398 | 10 | 2035.7814 | Planned | Planned | Replace poles
874 |  | 91416 | 2750 Ihunga Road | Gisborne | Mata 0304 | 2024-11-21 11:24 | 45617.475 | 2024-11-21 15:35 | 45617.6493 | 0.2024 | 0.00080636 | 21 | 5271 | Unplanned | Defective Equipment | Checked fuses H188 Puketoro side Ok. Drove the loop to fuses H272. Centre Hv DDO was burnt out. Replaced with new, held in when closed
875 |  | 1634 | 4378 Wharekopae Road | Gisborne | Tahora 1103 | 2024-11-21 12:32 | 45617.5222 | 2024-11-21 16:39 | 45617.6937 | 0.55009 | 0.0022271 | 58 | 14326 | Planned | Planned | Replace Pole D5060 - Urgent Work
876 |  | N/A 45 | Mata Road | Gisborne | Mata 0304 | 2024-11-21 15:27 | 45617.6438 | 2024-11-21 15:31 | 45617.6465 | 0.0046078 | 0.0011519 | 30 | 120 | Unplanned | Lightning | To Allow close on HV Fuses H272
877 |  | N/A 46 | Whangara/Glenroy/Waiomoko | Gisborne | Dalton 0502 | 2024-11-22 05:22 | 45618.2236 | 2024-11-22 09:14 | 45618.3847 | 0.75644 | 0.0067197 | 175 | 19700 | Unplanned | Unknown cause | Line Patrolled - no obvious fault found
878 |  | 91871 | Café 287, SH2 | Wairoa | Brickworks 3201 | 2024-11-22 05:49 | 45618.2424 | 2024-11-22 07:00 | 45618.2917 | 0.013631 | 0.00019199 | 5 | 355 | Unplanned | Adverse Weather | Patrol line. Replaced middle and right side HV fuses
879 |  | 3303 | Taumata Road | Gisborne | Tahora 1103 | 2024-11-22 08:30 | 45618.3542 | 2024-11-22 16:17 | 45618.6785 | 0.38667 | 0.00084476 | 22 | 5037.5946 | Planned | Planned | Replace Poles
880 |  | 3301 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2024-11-22 09:02 | 45618.3764 | 2024-11-22 15:57 | 45618.6646 | 0.43025 | 0.0010367 | 27 | 4838.0106 | Planned | Planned | Replace Poles
881 |  | 92006 | Kiore Bay Road, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2024-11-22 13:32 | 45618.5639 | 2024-11-22 16:47 | 45618.6993 | 0.059901 | 0.00030718 | 8 | 1560 | Unplanned | Wildlife | Un bine wire off pin let wires float cut head off pole
882 |  | 29764 | Rangikohua Road | Gisborne | Tauwhareparae 0404 | 2024-11-22 15:05 | 45618.6285 | 2024-11-22 16:47 | 45618.6993 | 0.025957 | 0.00030718 | 8 | 676 | Unplanned | Wildlife | Bird caused the fire on pole G1522
883 |  | 92086 | 200 Faulkner road | Gisborne | Tahora 1103 | 2024-11-22 17:27 | 45618.7271 | 2024-11-22 19:30 | 45618.8125 | 0.014169 | 0.00011519 | 3 | 369 | Unplanned | Unknown cause | Replace fuse
884 |  | 29765 | Wheatstone Road | Gisborne | Dalton 0502 | 2024-11-23 06:54 | 45619.2875 | 2024-11-23 09:34 | 45619.3986 | 1.5988 | 0.031525 | 821 | 41638 | Unplanned | Defective Equipment | Wire down failed crimp (cu) Steel conductor A3567 - A14
885 |  | 92578 | 109 Somerton Road | Gisborne | Haisman 0804 | 2024-11-23 09:55 | 45619.4132 | 2024-11-23 11:45 | 45619.4896 | 0.30411 | 0.0027647 | 72 | 7920 | Unplanned | Wildlife | Replace fuse
886 |  | 3307 | Wharekopae Road | Gisborne | Ngatapa 1102 | 2024-11-25 09:01 | 45621.3757 | 2024-11-25 15:49 | 45621.659 | 0.078332 | 0.00019199 | 5 | 1020.1958 | Planned | Planned | Replace poles
887 |  | 3306 | Kabul Street | Wairoa | Borough One 3204 | 2024-11-25 15:32 | 45621.6472 | 2024-11-25 17:22 | 45621.7236 | 1.1193 | 0.010175 | 265 | 14723.3076 | Planned | Planned | Replace X-arms
888 |  | 3447 | Waiomoko Road / Glenroy Rd / Pa Rd | Gisborne | Dalton 0502 | 2024-11-26 08:33 | 45622.3562 | 2024-11-26 11:05 | 45622.4618 | 0.50778 | 0.0033406 | 87 | 13224 | Planned | Planned | Remove ABS A271 - Urgent Work
889 |  | 3311 | Lottin Point Road | Gisborne | Hicks Bay 0102 | 2024-11-26 08:34 | 45622.3569 | 2024-11-26 14:31 | 45622.6049 | 0.15079 | 0.00042238 | 11 | 1964.406 | Planned | Planned | Replace Pole & Install TX H5493
890 |  | 3309 | Taylors Bay | Wairoa | Mahia 3301 | 2024-11-26 09:04 | 45622.3778 | 2024-11-26 16:07 | 45622.6715 | 0.77963 | 0.0018431 | 48 | 10170.7112 | Planned | Planned | Replace Poles
891 |  | 94426 | 1333 Ngakoroa Rd, Ormond | Gisborne | Waimata 0903 | 2024-11-26 10:45 | 45622.4479 | 2024-11-26 13:04 | 45622.5444 | 0.0053373 | 3.8398e-05 | 1 | 139 | Unplanned | Unknown cause | Possible tree hit lines yesterday by tree cutters in the area
892 |  | 29774 | Waimata Valley Road | Gisborne | Waimata 0903 | 2024-11-26 12:29 | 45622.5201 | 2024-11-26 15:58 | 45622.6653 | 0.048151 | 0.00023039 | 6 | 1254 | Unplanned | Human Error | Tree team (Arbc) dropped tree thru HV @ Pole G550
893 |  | 3310 | Glenelg Road | Gisborne | Waimata 0903 | 2024-11-26 12:32 | 45622.5222 | 2024-11-26 14:11 | 45622.591 | 0.0076028 | 7.6796e-05 | 2 | 99.0076 | Planned | Planned | Install new cable up pole D595
894 |  | 29778 | Freyberg / Kabul / Clyde | Wairoa | Borough One 3204 | 2024-11-27 08:05 | 45623.3368 | 2024-11-27 09:17 | 45623.3868 | 1.68 | 0.03141 | 818 | 43751 | Unplanned | Defective Equipment | Cable fault between W231 - W263
895 |  | 3308 | Wharekopae Road | Gisborne | Ngatapa 1102 | 2024-11-27 09:02 | 45623.3764 | 2024-11-27 15:01 | 45623.6257 | 0.068924 | 0.00019199 | 5 | 897.6723 | Planned | Planned | Replace Poles
896 |  | 3312 | Moana Road | Gisborne | Dalton 0502 | 2024-11-27 09:12 | 45623.3833 | 2024-11-27 10:19 | 45623.4299 | 0.092616 | 0.0013823 | 36 | 1207.6671 | Planned | Planned | Replace LA on Crucifix
897 |  | 3313 | Winifred Road | Gisborne | Dalton 0502 | 2024-11-27 11:11 | 45623.466 | 2024-11-27 12:00 | 45623.5 | 0.088431 | 0.0018047 | 47 | 1153.5781 | Planned | Planned | Replace LA on Crucifix
898 |  | 3314 | Wairere Road | Gisborne | Tamarau 0503 | 2024-11-27 13:32 | 45623.5639 | 2024-11-27 14:07 | 45623.5882 | 0.080636 | 0.0023039 | 60 | 1052.4191 | Planned | Planned | Replace LA on Crucifix
899 |  | 95129 | 8km marker Arikihi Road, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2024-11-27 15:18 | 45623.6375 | 2024-11-27 17:07 | 45623.7132 | 0.012556 | 0.00011519 | 3 | 327 | Unplanned | Unknown cause | Replace fuse
900 |  | 3318 | Tyndall / Rutene Rd cnr | Gisborne | Wainui 0504 | 2024-11-28 06:59 | 45624.291 | 2024-11-28 08:09 | 45624.3396 | 0.0026879 | 3.8398e-05 | 1 | 15.5006 | Planned | Planned | Install Stubb pole
901 |  | 3315 | Waikura Valley Road | Gisborne | Hicks Bay 0102 | 2024-11-28 08:34 | 45624.3569 | 2024-11-28 15:29 | 45624.6451 | 0.62147 | 0.0014975 | 39 | 8104.6187 | Planned | Planned | Replace poles
902 |  | 3317 | Frasertown Road | Wairoa | Nuhaka 3203 | 2024-11-28 08:37 | 45624.359 | 2024-11-28 11:49 | 45624.4924 | 0.30964 | 0.0016127 | 42 | 4039.1121 | Planned | Planned | Upgrade TX W1759
903 |  | 3316 | Waikura Valley Road | Gisborne | Hicks Bay 0102 | 2024-11-29 08:33 | 45625.3562 | 2024-11-29 11:58 | 45625.4986 | 0.30699 | 0.0014975 | 39 | 4008.0126 | Planned | Planned | Replace Poles
904 |  | 3321 | Whakato Road | Gisborne | Muriwai 0905 | 2024-11-29 09:01 | 45625.3757 | 2024-11-29 15:49 | 45625.659 | 1.4413 | 0.0035326 | 92 | 18834.3002 | Planned | Planned | Replace poles upgrade TX install new TX
905 |  | N/A 47 | Tolaga Bay 50kV | Gisborne | Rototahi 0403 | 2024-11-30 06:30 | 45626.2708 | 2024-11-30 06:50 | 45626.2847 | 0.16588 | 0.008294 | 216 | 4320 | Unplanned | Unknown cause | LFI on Centre phase Tolaga - Tokomaru 50kV Plashing. Restored Tolaga Bay to Norman 0853. Aerial Patrol Tol-Tok 50kV Monday 2/12: Unable to identify fault cause. Closed G6L
906 |  | N/A 47 | Tolaga Bay 50kV | Gisborne | Town 0402 | 2024-11-30 06:30 | 45626.2708 | 2024-11-30 07:00 | 45626.2917 | 0.23615 | 0.0078716 | 205 | 6150 | Unplanned | Unknown cause | LFI on Centre phase Tolaga - Tokomaru 50kV Plashing. Restored Tolaga Bay to Norman 0853. Aerial Patrol Tol-Tok 50kV Monday 2/12: Unable to identify fault cause. Closed G6L
907 |  | N/A 47 | Tolaga Bay 50kV | Gisborne | Toko Tie 0401 | 2024-11-30 06:30 | 45626.2708 | 2024-11-30 07:01 | 45626.2924 | 0.099988 | 0.0032254 | 84 | 2604 | Unplanned | Unknown cause | LFI on Centre phase Tolaga - Tokomaru 50kV Plashing. Restored Tolaga Bay to Norman 0853. Aerial Patrol Tol-Tok 50kV Monday 2/12: Unable to identify fault cause. Closed G6L
908 |  | N/A 47 | Tolaga Bay 50kV | Gisborne | Tauwhareparae 0404 | 2024-11-30 06:30 | 45626.2708 | 2024-11-30 07:09 | 45626.2979 | 0.19257 | 0.0056061 | 146 | 5015 | Unplanned | Unknown cause | LFI on Centre phase Tolaga - Tokomaru 50kV Plashing. Restored Tolaga Bay to Norman 0853. Aerial Patrol Tol-Tok 50kV Monday 2/12: Unable to identify fault cause. Closed G6L
909 |  | 96699 | 1945 Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2024-11-30 07:30 | 45626.3125 | 2024-11-30 09:35 | 45626.3993 | 0.0047998 | 3.8398e-05 | 1 | 125 | Unplanned | Defective Equipment | Replaced fuse holder & DDO fuse
910 |  | 97666 | 599 Arakihi Road, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2024-12-01 10:57 | 45627.4563 | 2024-12-01 12:15 | 45627.5104 | 0.0089851 | 0.00011519 | 3 | 234 | Unplanned | Unknown cause | Fuse fault
911 |  | 3448 | Seeka Coolstore | Gisborne | Chalmers 0707 | 2024-12-02 08:29 | 45628.3535 | 2024-12-03 10:48 | 45629.45 | 0.12126 | 7.6796e-05 | 2 | 3158 | Planned | Planned | New metering not onsite by 2/12. Outage ran overnight to allow for new metering on 3/12. Equipment did not arrive as planned. Site restored until new equipment available
912 |  | 3319 | Nelson Road | Gisborne | Haisman 0804 | 2024-12-02 09:15 | 45628.3854 | 2024-12-02 11:30 | 45628.4792 | 0.34205 | 0.0025343 | 66 | 3473.5192 | Planned | Planned | To cut in 11kV line breaks @ C5735
913 |  | 98794 | 326 Matokitoki Valley Road | Gisborne | Whangara 0506 | 2024-12-03 05:52 | 45629.2444 | 2024-12-03 07:30 | 45629.3125 | 0.011289 | 0.00011519 | 3 | 294 | Unplanned | Unknown cause | Replace fuse
914 |  | 99476 | 3100 Mata Rd, Huiarus | Gisborne | Mata 0304 | 2024-12-03 07:39 | 45629.3187 | 2024-12-04 18:10 | 45630.7569 | 0.15904 | 7.6796e-05 | 2 | 4142 | Unplanned | Adverse Weather | Replace Fuse - Rang Customer. Ok to attend later in the day. Still wingy. Running on generator
915 |  | 3322 | Rotoparu Road | Wairoa | Frasertown 3103 | 2024-12-03 08:34 | 45629.3569 | 2024-12-03 14:47 | 45629.616 | 0.085935 | 0.00023039 | 6 | 1119.2578 | Planned | Planned | Cutting trees
916 |  | 3325 | Woodland Rd / Kakariki Rd | Wairoa | Raupunga 3101 | 2024-12-03 09:46 | 45629.4069 | 2024-12-03 10:33 | 45629.4396 | 0.019852 | 0.00042238 | 11 | 258.6092 | Planned | Planned | Install fault indicators between W1015 & W5300
917 |  | 29818 | Matokitoki Valley Road | Gisborne | Whangara 0506 | 2024-12-03 16:09 | 45629.6729 | 2024-12-03 17:07 | 45629.7132 | 0.084629 | 0.0014591 | 38 | 2204 | Unplanned | Defective Equipment | Replace HV fuse TX B79
918 |  | 3323 | Te Araroa | Gisborne | Te Araroa Sub 01 | 2024-12-03 17:06 | 45629.7125 | 2024-12-03 17:07 | 45629.7132 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | 50kV pole changes
919 |  | 3323 | Te Araroa | Gisborne | Awatere 0101 | 2024-12-03 17:06 | 45629.7125 | 2024-12-03 17:07 | 45629.7132 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | 50kV pole changes
920 |  | 3323 | Te Araroa | Gisborne | Hicks Bay 0102 | 2024-12-03 17:06 | 45629.7125 | 2024-12-03 17:07 | 45629.7132 | 0.0096763 | 0.0096763 | 252 | 127.2192 | Planned | Planned | 50kV pole changes
921 |  | 3323 | Te Araroa | Gisborne | Te Araroa 0103 | 2024-12-03 17:06 | 45629.7125 | 2024-12-03 17:07 | 45629.7132 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | 50kV pole changes
922 |  | 3326 | Taumata Road | Gisborne | Tahora 1103 | 2024-12-04 08:31 | 45630.3549 | 2024-12-04 15:14 | 45630.6347 | 0.10832 | 0.00026879 | 7 | 1410.8791 | Planned | Planned | To replace poles
923 |  | 3324 | Nelson Road | Gisborne | Haisman 0804 | 2024-12-04 09:00 | 45630.375 | 2024-12-04 11:23 | 45630.4743 | 0.3624 | 0.0025343 | 66 | 4730.9592 | Planned | Planned | To close 11kv line breaks @ Pole C5735
924 |  | 3454 A | Morere Road | Wairoa | Morere 3401 | 2024-12-04 10:49 | 45630.4507 | 2024-12-04 11:00 | 45630.4583 | 0.016895 | 0.0015359 | 40 | 440 | Planned | Planned | To install 1kVA TX @ Remote switch W810
925 |  | 3454 | Morere Road | Wairoa | Morere 3401 | 2024-12-04 11:00 | 45630.4583 | 2024-12-04 13:58 | 45630.5819 | 1.1141 | 0.0062589 | 163 | 29014 | Planned | Planned | To install 1kVA TX @ Remote switch W810
926 |  | 3454 B | Morere Road | Wairoa | Morere 3401 | 2024-12-04 14:00 | 45630.5833 | 2024-12-04 14:04 | 45630.5861 | 0.0061437 | 0.0015359 | 40 | 160 | Planned | Planned | To install 1kVA TX @ Remote switch W810
927 |  | 100168 | 77 Matukoa Road | Gisborne | Hicks Bay 0102 | 2024-12-05 08:15 | 45631.3438 | 2024-12-05 11:15 | 45631.4688 | 0.055293 | 0.00030718 | 8 | 1440 | Unplanned | Unknown cause | Replace fuse
928 |  | 3441 | Black Street, Victoria Street | Wairoa | Borough One 3204 | 2024-12-05 09:03 | 45631.3771 | 2024-12-05 16:03 | 45631.6687 | 0.9515 | 0.0022655 | 59 | 12418.0693 | Planned | Planned | Replace Link Box 11842
929 |  | 3328 | Mangatu Road | Gisborne | Whatatutu 1201 | 2024-12-05 09:07 | 45631.3799 | 2024-12-05 13:17 | 45631.5535 | 0.24959 | 0.00099835 | 26 | 3032.024 | Planned | Planned | Cut trees
930 |  | 3442 | Waihi Road | Wairoa | Frasertown 3103 | 2024-12-05 09:33 | 45631.3979 | 2024-12-05 10:43 | 45631.4465 | 0.010751 | 0.00015359 | 4 | 140.0215 | Planned | Planned | Replace TX W171
931 |  | 3330 | Whaanga Street | Wairoa | Morere 3401 | 2024-12-05 10:13 | 45631.4257 | 2024-12-05 12:25 | 45631.5174 | 0.060822 | 0.00046078 | 12 | 1584 | Planned | Planned | Install LV road x-ing pole opp W1266
932 |  | 29852 | Arakihi Road | Gisborne | Tauwhareparae 0404 | 2024-12-05 15:00 | 45631.625 | 2024-12-05 16:40 | 45631.6944 | 0.011519 | 0.00011519 | 3 | 300 | Unplanned | Defective Equipment | Faulty Transformer G266
933 |  | 3329 | Waiapu Road | Gisborne | Te Araroa Sub 01 | 2024-12-05 17:07 | 45631.7132 | 2024-12-05 17:08 | 45631.7139 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Replacing 50kV Poles
934 |  | 3329 | Waiapu Road | Gisborne | Awatere 0101 | 2024-12-05 17:07 | 45631.7132 | 2024-12-05 17:08 | 45631.7139 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | Replacing 50kV Poles
935 |  | 3329 | Waiapu Road | Gisborne | Hicks Bay 0102 | 2024-12-05 17:07 | 45631.7132 | 2024-12-05 17:08 | 45631.7139 | 0.0096763 | 0.0096763 | 252 | 127.2192 | Planned | Planned | Replacing 50kV Poles
936 |  | 3329 | Waiapu Road | Gisborne | Te Araroa 0103 | 2024-12-05 17:07 | 45631.7132 | 2024-12-05 17:08 | 45631.7139 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | Replacing 50kV Poles
937 |  | 100431 | 1737 Ohuka Road | Wairoa | Ruakituri 2003 | 2024-12-05 17:57 | 45631.7479 | 2024-12-05 19:00 | 45631.7917 | 0.024191 | 0.00038398 | 10 | 630 | Unplanned | Unknown cause | Replace fuse
938 |  | 3327 | Taumata Road | Gisborne | Tahora 1103 | 2024-12-06 08:32 | 45632.3556 | 2024-12-06 16:40 | 45632.6944 | 0.13117 | 0.00026879 | 7 | 1673.4497 | Planned | Planned | Replace 11kV poles
939 |  | 101800 | 1945 Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2024-12-07 15:40 | 45633.6528 | 2024-12-07 17:50 | 45633.7431 | 0.0049917 | 3.8398e-05 | 1 | 130 | Unplanned | Defective Equipment | HV tube just sitting in S/S holder & Blown. Couldn't get new fuse wire in. Replaced with new Betacom HV tube +2a HV DDI Link
940 |  | 3335 | Lahore Street | Wairoa | Borough Two 3205 | 2024-12-08 09:03 | 45634.3771 | 2024-12-08 16:17 | 45634.6785 | 1.0665 | 0.0024575 | 64 | 13922.1294 | Planned | Planned | Replace RMU W263 / W264 / W265
941 |  | 29854 | Wharerata Road | Gisborne | Muriwai 0905 | 2024-12-08 21:35 | 45634.8993 | 2024-12-09 12:33 | 45635.5229 | 0.99455 | 0.0094843 | 247 | 25901 | Unplanned | Vegetation | Tree fell on the line which broke the conductor at pole C3566
942 |  | N/A 48 | Massey Road | Gisborne | Aberdeen 0609 | 2024-12-10 08:26 | 45636.3514 | 2024-12-10 09:35 | 45636.3993 | 2.2351 | 0.055332 | 1441 | 58208 | Unplanned | Third Party Interference | Cable damaged by contractor working on the bridge at Massey Road
943 |  | 3443 | Waiapu Road, Hicks Bay | Gisborne | Te Araroa Sub 01 | 2024-12-10 17:08 | 45636.7139 | 2024-12-10 17:09 | 45636.7146 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Replace 50kV poles - run generator
944 |  | 3443 | Waiapu Road, Hicks Bay | Gisborne | Awatere 0101 | 2024-12-10 17:08 | 45636.7139 | 2024-12-10 17:09 | 45636.7146 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | Replace 50kV poles - run generator
945 |  | 3443 | Waiapu Road, Hicks Bay | Gisborne | Hicks Bay 0102 | 2024-12-10 17:08 | 45636.7139 | 2024-12-10 17:09 | 45636.7146 | 0.0096763 | 0.0096763 | 252 | 127.2192 | Planned | Planned | Replace 50kV poles - run generator
946 |  | 3443 | Waiapu Road, Hicks Bay | Gisborne | Te Araroa 0103 | 2024-12-10 17:08 | 45636.7139 | 2024-12-10 17:09 | 45636.7146 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | Replace 50kV poles - run generator
947 |  | 3476 | Bright Street | Gisborne | Port A 1501 | 2024-12-11 06:00 | 45637.25 | 2024-12-11 06:11 | 45637.2576 | 0.013094 | 0.0011903 | 31 | 341 | Planned | Planned | Isolate TX B167 to liven RMU B1047 - Urgent
948 |  | 3340 | Taumata Road | Gisborne | Tahora 1103 | 2024-12-11 08:32 | 45637.3556 | 2024-12-11 15:42 | 45637.6542 | 0.11558 | 0.00026879 | 7 | 1505.4045 | Planned | Planned | 11kV Pole changes
949 |  | 3333 | Fox Street | Gisborne | Whangara 0506 | 2024-12-11 09:04 | 45637.3778 | 2024-12-11 10:24 | 45637.4333 | 0.26418 | 0.0033022 | 86 | 3451.3597 | Planned | Planned | Replace 11kV insulator stand offs on pole
950 |  | 3331 | Riverside Road | Gisborne | Harris 1502 | 2024-12-11 11:07 | 45637.4632 | 2024-12-11 11:31 | 45637.4799 | 0.052529 | 0.0021887 | 57 | 685.4971 | Planned | Planned | Replace standoff insulators on pole B2079
951 |  | 3332 | Stafford Street | Gisborne | Harris 1502 | 2024-12-11 12:30 | 45637.5208 | 2024-12-11 13:00 | 45637.5417 | 0.12095 | 0.0040318 | 105 | 1581.3501 | Planned | Planned | Replace 11kV insulator cable stand offs on pole
952 |  | 3334 | Harris Street | Gisborne | Harris 1502 | 2024-12-11 14:02 | 45637.5847 | 2024-12-11 14:22 | 45637.5986 | 0.056061 | 0.0028031 | 73 | 732.0462 | Planned | Planned | Replace 11kV cable stand-off
953 |  | 3445 | Ngakaroa Road | Gisborne | Waimata 0903 | 2024-12-12 09:02 | 45638.3764 | 2024-12-12 16:00 | 45638.6667 | 0.35311 | 0.00084476 | 22 | 4601.8842 | Planned | Planned | To remove trees
954 |  | 3444 | Waiapu Road | Gisborne | Te Araroa Sub 01 | 2024-12-12 17:39 | 45638.7354 | 2024-12-12 17:40 | 45638.7361 | 3.8398e-05 | 3.8398e-05 | 1 | 0 | Planned | Planned | Replaced 50kV poles. Outage for Te Araroa feeders when changing back from islanded generator to main supply
955 |  | 3444 | Waiapu Road | Gisborne | Awatere 0101 | 2024-12-12 17:39 | 45638.7354 | 2024-12-12 17:40 | 45638.7361 | 0.0034942 | 0.0034942 | 91 | 0 | Planned | Planned | Replaced 50kV poles. Outage for Te Araroa feeders when changing back from islanded generator to main supply
956 |  | 3444 | Waiapu Road | Gisborne | Hicks Bay 0102 | 2024-12-12 17:39 | 45638.7354 | 2024-12-12 17:40 | 45638.7361 | 0.0096763 | 0.0096763 | 252 | 0 | Planned | Planned | Replaced 50kV poles. Outage for Te Araroa feeders when changing back from islanded generator to main supply
957 |  | 3444 | Waiapu Road | Gisborne | Te Araroa 0103 | 2024-12-12 17:39 | 45638.7354 | 2024-12-12 17:40 | 45638.7361 | 0.0049533 | 0.0049533 | 129 | 0 | Planned | Planned | Replaced 50kV poles. Outage for Te Araroa feeders when changing back from islanded generator to main supply
958 |  | 29844 | YMCA Road | Wairoa | Mahia 3301 | 2024-12-12 18:00 | 45638.75 | 2024-12-12 18:36 | 45638.775 | 0.0013823 | 3.8398e-05 | 1 | 36 | Unplanned | Defective Equipment | Jumper off @ TX W1516
959 |  | N/A 59 | Tuai | Wairoa | Tuai Sub | 2024-12-13 05:59 | 45639.2493 | 2024-12-13 06:16 | 45639.2611 | 0.00065277 | 3.8398e-05 | 1 | 17 | Unplanned | Defective Equipment | W53 fail to Trip on Scada. 110kV CB 302 Trip under Intertrip
960 |  | N/A 59 | Tuai | Wairoa | Lake | 2024-12-13 05:59 | 45639.2493 | 2024-12-13 06:16 | 45639.2611 | 0.0065277 | 0.00038398 | 10 | 170 | Unplanned | Defective Equipment | W53 fail to Trip on Scada. 110kV CB 302 Trip under Intertrip
961 |  | N/A 59 | Tuai | Wairoa | Village 2002 | 2024-12-13 05:59 | 45639.2493 | 2024-12-13 06:16 | 45639.2611 | 0.11619 | 0.0068349 | 178 | 3026 | Unplanned | Defective Equipment | W53 fail to Trip on Scada. 110kV CB 302 Trip under Intertrip
962 |  | N/A 59 | Tuai | Wairoa | Ruakituri 2003 | 2024-12-13 05:59 | 45639.2493 | 2024-12-13 06:16 | 45639.2611 | 0.10575 | 0.0062205 | 162 | 2754 | Unplanned | Defective Equipment | W53 fail to Trip on Scada. 110kV CB 302 Trip under Intertrip
963 |  | 29878 | YMCA Road | Wairoa | Mahia 3301 | 2024-12-13 11:52 | 45639.4944 | 2024-12-13 19:45 | 45639.8229 | 0.018162 | 3.8398e-05 | 1 | 473 | Unplanned | Defective Equipment | To replace faulty transformer W1516
964 |  | 3449 | Riverside Road | Gisborne | Waimata 0903 | 2024-12-14 09:05 | 45640.3785 | 2024-12-14 11:07 | 45640.4632 | 0.042161 | 0.00034558 | 9 | 549.2799 | Planned | Planned | Install new TX
965 |  | 105562 | 362 Whakaangiangi Road | Gisborne | Awatere 0101 | 2024-12-14 11:09 | 45640.4646 | 2024-12-14 14:15 | 45640.5938 | 0.007142 | 3.8398e-05 | 1 | 186 | Unplanned | Unknown cause | Replace fuse
966 |  | 29879 | Back Ormond Road | Gisborne | Waimata 0903 | 2024-12-14 17:38 | 45640.7347 | 2024-12-14 21:30 | 45640.8958 | 0.12683 | 0.00069116 | 18 | 3303 | Unplanned | Defective Equipment | Blown cable termination
967 |  | 29846 | Motu | Gisborne | Matawai 1204 | 2024-12-14 17:51 | 45640.7438 | 2024-12-17 16:04 | 45643.6694 | 0.98203 | 0.004723 | 123 | 25575 | Unplanned | Defective Equipment | HW Pole broke, needed bucket truck to cut jumpers. Install generator at TX F120 - High Winds
968 |  | 29883 | Wharerata Road / Paritu Road | Gisborne | Muriwai 0905 | 2024-12-16 03:01 | 45642.1257 | 2024-12-20 12:09 | 45646.5062 | 0.8203 | 0.0054141 | 141 | 21363 | Unplanned | Vegetation | Pole down @ C3775 (Btwn C184 & C189) L/break @ Pole C3768. Pole down byd HV fuses C3145 (Genset @ TX C190 1 x customer off byd C3145)
969 |  | 107633 | 503 Lake Road, Patutahi | Gisborne | Lavenham 0902 | 2024-12-16 05:24 | 45642.225 | 2024-12-16 09:22 | 45642.3903 | 0.054832 | 0.00023039 | 6 | 1428 | Unplanned | Unknown cause | D2045 access very limited with new native growth
970 |  | 3451 A | Waiapu road | Gisborne | Te Araroa Sub 01 | 2024-12-16 17:12 | 45642.7167 | 2024-12-16 17:13 | 45642.7174 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Replace 50kV Poles
971 |  | 3451 A | Waiapu road | Gisborne | Awatere 0101 | 2024-12-16 17:12 | 45642.7167 | 2024-12-16 17:13 | 45642.7174 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | Replace 50kV Poles
972 |  | 3451 A | Waiapu road | Gisborne | Hicks Bay 0102 | 2024-12-16 17:12 | 45642.7167 | 2024-12-16 17:13 | 45642.7174 | 0.0096763 | 0.0096763 | 252 | 127.2192 | Planned | Planned | Replace 50kV Poles
973 |  | 3451 A | Waiapu road | Gisborne | Te Araroa 0103 | 2024-12-16 17:12 | 45642.7167 | 2024-12-16 17:13 | 45642.7174 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | Replace 50kV Poles
974 |  | 3451 A | Waiapu road | Gisborne | Ruatoria Sub 02 | 2024-12-16 17:12 | 45642.7167 | 2024-12-16 17:13 | 45642.7174 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Replace 50kV Poles
975 |  | 3451 A | Waiapu road | Gisborne | Ruatoria 0201 | 2024-12-16 17:12 | 45642.7167 | 2024-12-16 17:13 | 45642.7174 | 0.011827 | 0.011827 | 308 | 155.8213 | Planned | Planned | Replace 50kV Poles
976 |  | 3451 A | Waiapu road | Gisborne | Makarika 0204 | 2024-12-16 17:12 | 45642.7167 | 2024-12-16 17:13 | 45642.7174 | 0.004339 | 0.004339 | 113 | 56.7452 | Planned | Planned | Replace 50kV Poles
977 |  | 3451 A | Waiapu road | Gisborne | Tiki Tiki 0206 | 2024-12-16 17:12 | 45642.7167 | 2024-12-16 17:13 | 45642.7174 | 0.012134 | 0.012134 | 316 | 159.9171 | Planned | Planned | Replace 50kV Poles
978 |  | 3451 A | Waiapu road | Gisborne | Inland 0301 | 2024-12-16 17:12 | 45642.7167 | 2024-12-16 17:13 | 45642.7174 | 0.0046462 | 0.0046462 | 121 | 60.7811 | Planned | Planned | Replace 50kV Poles
979 |  | 108419 | 418 Waiatai Road | Wairoa | Nuhaka 3203 | 2024-12-17 06:40 | 45643.2778 | 2024-12-17 08:20 | 45643.3472 | 0.053757 | 0.00053757 | 14 | 1400 | Unplanned | Unknown cause | Replace fuses
980 |  | N/A 50 | North Clyde / McLean St / Tawhara Valley | Wairoa | Brickworks 3201 | 2024-12-17 07:45 | 45643.3229 | 2024-12-17 10:05 | 45643.4201 | 1.4764 | 0.046654 | 1215 | 38450 | Unplanned | Adverse Weather | Line patrol unable to identify any fault cause. Suspect wind clashing conductor at sewage plant
981 |  | N/A 50 | North Clyde / McLean St / Tawhara Valley | Wairoa | Borough One 3204 | 2024-12-17 08:52 | 45643.3694 | 2024-12-17 08:58 | 45643.3736 | 0.18869 | 0.031448 | 819 | 4914 | Unplanned | Adverse Weather | Line patrol unable to identify any fault cause. Suspect wind clashing conductor at sewage plant
982 |  | 29886 | 1851 Tiniroto Road | Gisborne | W O Kuri 1001 | 2024-12-17 09:06 | 45643.3792 | 2024-12-17 10:27 | 45643.4354 | 0.012441 | 0.00015359 | 4 | 324 | Unplanned | Vegetation | Tree through LV Lines
983 |  | 3455 | 116A Darwin Road | Gisborne | Whangara 0506 | 2024-12-17 09:13 | 45643.384 | 2024-12-17 10:50 | 45643.4514 | 0.055869 | 0.00057597 | 15 | 727.919 | Planned | Planned | Cut in new distribution box
984 |  | 108555 | 1001 Tahora Rd | Gisborne | Tahora 1103 | 2024-12-17 10:36 | 45643.4417 | 2024-12-17 18:10 | 45643.7569 | 0.41838 | 0.00092155 | 24 | 10896 | Unplanned | Adverse Weather | Replace fuses
985 |  | 108572 | 63 Thomas Rd | Gisborne | Rototahi 0403 | 2024-12-17 11:21 | 45643.4729 | 2024-12-18 | 45644 | 0.087432 | 0.00011519 | 3 | 2277 | Unplanned | Vegetation | Replace fuses
986 |  | 29889 | Tiniroto Rd / Ruakaka Rd | Gisborne | Tiniroto 1003 | 2024-12-17 12:06 | 45643.5042 | 2024-12-17 16:16 | 45643.6778 | 0.46707 | 0.0032638 | 85 | 12164 | Unplanned | Vegetation | Tree through line @ Pole D3290 - High Winds
987 |  | 108657 | 1370 Rangitukia road, Tikitiki | Gisborne | Tiki Tiki 0206 | 2024-12-17 13:51 | 45643.5771 | 2024-12-17 18:50 | 45643.7847 | 0.55109 | 0.0018431 | 48 | 14352 | Unplanned | Vegetation | Cut 8 x branches out of 11kV
988 |  | 29891 | 341 East Coast Road | Wairoa | Mahia 3301 | 2024-12-17 15:22 | 45643.6403 | 2024-12-17 19:54 | 45643.8292 | 0.093998 | 0.00034558 | 9 | 2448 | Unplanned | Defective Equipment | TX W1788 x-arm failure
989 |  | N/A 49 | Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2024-12-17 15:54 | 45643.6625 | 2024-12-17 18:48 | 45643.7833 | 0.32408 | 0.004147 | 108 | 8440 | Unplanned | Vegetation | Trees contacting o/head 11kV @ Pole J1189
990 |  | 29951 | SH2 Nuhaka - Morere | Wairoa | Morere 3401 | 2024-12-17 15:57 | 45643.6646 | 2024-12-18 13:39 | 45644.5687 | 0.71881 | 0.0032638 | 85 | 18720 | Unplanned | Vegetation | Tree through HV @ Pole W962 - High Winds
991 |  | 108812 | 1734 Bushy Knoll Road | Gisborne | Tiniroto 1003 | 2024-12-17 18:18 | 45643.7625 | 2024-12-18 15:02 | 45644.6264 | 0.23884 | 0.00019199 | 5 | 6220 | Unplanned | Vegetation | Trees making contact in zone
992 |  | 29892 | Kaiwitri Road | Gisborne | Waimata 0903 | 2024-12-17 18:26 | 45643.7681 | 2024-12-17 20:13 | 45643.8424 | 0.0082172 | 7.6796e-05 | 2 | 214 | Unplanned | Vegetation | Tree in LV
993 |  | 29895 | Motu Road, Matohora Road | Gisborne | Matawai 1204 | 2024-12-18 07:50 | 45644.3264 | 2024-12-18 15:25 | 45644.6424 | 0.4617 | 0.0023423 | 61 | 12024 | Unplanned | Vegetation | Tree through 11kV before TX F118
994 |  | 29952 | Waiatai Road | Wairoa | Nuhaka 3203 | 2024-12-18 08:30 | 45644.3542 | 2024-12-18 10:01 | 45644.4174 | 0.048919 | 0.00053757 | 14 | 1274 | Unplanned | Vegetation | Trees brought down HV conductor - High Winds
995 |  | 3481 | Waihi Road | Wairoa | Frasertown 3103 | 2024-12-18 09:00 | 45644.375 | 2024-12-18 13:23 | 45644.5576 | 0.99977 | 0.0038014 | 99 | 26037 | Planned | Planned | Cut tree on 50kV line
996 |  | N/A 51 | Onepoto Road | Gisborne | Hicks Bay 0102 | 2024-12-18 10:02 | 45644.4181 | 2024-12-18 15:04 | 45644.6278 | 0.59141 | 0.0019583 | 51 | 15402 | Unplanned | Vegetation | Trees in line
997 |  | 29955 | Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2024-12-18 16:17 | 45644.6785 | 2024-12-18 17:45 | 45644.7396 | 0.17602 | 0.004147 | 108 | 4584 | Unplanned | Vegetation | Trees in Line @ Pole J1245 - High Winds
998 |  | 29897 | Dunston Road | Gisborne | Dunstan 1403 | 2024-12-18 18:37 | 45644.7757 | 2024-12-18 19:21 | 45644.8063 | 0.013516 | 0.00030718 | 8 | 352 | Unplanned | Defective Equipment | Broken 11kV Jumper Lineside TX C3965 Fuses
999 |  | 29956 | Waimata Valley Road | Gisborne | Waimata 0903 | 2024-12-19 12:57 | 45645.5396 | 2025-01-14 13:27 | 45671.5604 | 0.37377 | 0.003763 | 98 | 9734 | Unplanned | Vegetation | Wires down @ Pole E1213 & Pole E1215 - High Winds
1000 |  | N/A 52 | Waipiro Rd / Kopuaroa Rd | Gisborne | Inland 0301 | 2024-12-19 16:31 | 45645.6882 | 2024-12-20 17:17 | 45646.7201 | 0.36739 | 0.0039934 | 104 | 9568 | Unplanned | Vegetation | Trees through HV lines @ H2216 - H2214, H1977
1001 |  | 110708 | B79 Matoketoke Valley Rd | Gisborne | Whangara 0506 | 2024-12-20 15:31 | 45646.6465 | 2024-12-20 16:11 | 45646.6743 | 0.0015359 | 3.8398e-05 | 1 | 40 | Unplanned | Unknown cause | Replace fuses
1002 |  | 111229 | 404 Armstrong Road | Gisborne | Whatatutu 1201 | 2024-12-21 08:20 | 45647.3472 | 2024-12-21 14:00 | 45647.5833 | 0.013055 | 3.8398e-05 | 1 | 340 | Unplanned | Unknown cause | Replace fuse
1003 |  | N/A 60 | Caves Rd, Matokitiki Valley Road | Gisborne | Whangara 0506 | 2024-12-22 11:15 | 45648.4688 | 2024-12-22 15:35 | 45648.6493 | 0.1842 | 0.0016895 | 44 | 4797 | Unplanned | Vegetation | Tree branch hanging on line at Pole A3478 - A3479
1004 |  | 113109 | 78 Matakaoa Road | Gisborne | Hicks Bay 0102 | 2024-12-22 17:10 | 45648.7153 | 2024-12-22 20:00 | 45648.8333 | 0.052221 | 0.00030718 | 8 | 1360 | Unplanned | Unknown cause | Replace fuse
1005 |  | 113441 | 532 Waiatai Road | Wairoa | Nuhaka 3203 | 2024-12-23 07:02 | 45649.2931 | 2024-12-23 08:30 | 45649.3542 | 0.047306 | 0.00053757 | 14 | 1232 | Unplanned | Unknown cause | Replace fuses
1006 |  | 114324 | 597 Whakarau Road | Gisborne | Matawai 1204 | 2024-12-24 07:06 | 45650.2958 | 2024-12-24 10:00 | 45650.4167 | 0.0066813 | 3.8398e-05 | 1 | 174 | Unplanned | Wildlife | Replace fuse
1007 |  | 115098 | 209 Erepiti Road | Wairoa | Ruakituri 2003 | 2024-12-25 09:37 | 45651.4007 | 2024-12-25 11:30 | 45651.4792 | 0.004339 | 3.8398e-05 | 1 | 113 | Unplanned | Unknown cause | Replace fuse
1008 |  | 116541 | Waiatai Road | Wairoa | Nuhaka 3203 | 2024-12-26 19:15 | 45652.8021 | 2024-12-28 20:00 | 45654.8333 | 1.5724 | 0.00053757 | 14 | 40950 | Unplanned | Vegetation | Replace fuse
1009 |  | 29985 | Ruakituri | Wairoa | Ruakituri 2003 | 2024-12-27 05:21 | 45653.2229 | 2025-01-10 12:52 | 45667.5361 | 9.5092 | 0.035941 | 936 | 247649 | Unplanned | Adverse Weather | High Winds - conductor clashing
1010 |  | 29962 | Ihungia Road | Gisborne | Mata 0304 | 2024-12-27 06:16 | 45653.2611 | 2024-12-28 16:22 | 45654.6819 | 0.27516 | 0.00061437 | 16 | 7166 | Unplanned | Vegetation | Tree thru line
1011 |  | N/A 61 | North Clyde / McLean St / Tawhara Valley | Wairoa | Brickworks 3201 | 2024-12-27 07:02 | 45653.2931 | 2024-12-27 21:44 | 45653.9056 | 2.5255 | 0.023692 | 617 | 65772 | Unplanned | Adverse Weather | Conductor clashing during heavy wind - at sewage plant
1012 |  | 29917 | Maungatiaki Road | Wairoa | Nuhaka 3203 | 2024-12-27 08:10 | 45653.3403 | 2024-12-30 20:57 | 45656.8729 | 2.8815 | 0.01367 | 356 | 75044 | Unplanned | Vegetation | Tree through line @ Pole W1761
1013 |  | 29963 | Kaiwaitau Road | Wairoa | Mahia 3301 | 2024-12-27 09:35 | 45653.3993 | 2024-12-28 11:58 | 45654.4986 | 2.4619 | 0.0048382 | 126 | 64114 | Unplanned | Adverse Weather | High winds brought down conductor
1014 |  | 29965 | Tiniroto | Gisborne | Tiniroto 1003 | 2024-12-27 11:12 | 45653.4667 | 2024-12-28 16:05 | 45654.6701 | 3.3799 | 0.0095227 | 248 | 88022 | Unplanned | Vegetation | Trees thru lines D2348 - D3249
1015 |  | 29969 | Mangaone Road | Wairoa | Morere 3401 | 2024-12-27 11:30 | 45653.4792 | 2024-12-28 18:58 | 45654.7903 | 0.79745 | 0.00042238 | 11 | 20768 | Unplanned | Vegetation | Tree thru line
1016 |  | 116609 | 987 Mangpoike Road | Wairoa | Frasertown 3103 | 2024-12-27 12:28 | 45653.5194 | 2024-12-28 18:20 | 45654.7639 | 0.20643 | 0.00011519 | 3 | 5376 | Unplanned | Defective Equipment | Replace fuse
1017 |  | 116670 | 2601 Wharekopae Road | Gisborne | Ngatapa 1102 | 2024-12-27 13:42 | 45653.5708 | 2024-12-27 14:45 | 45653.6146 | 0.0096763 | 0.00015359 | 4 | 252 | Unplanned | Unknown cause | Replace fuses
1018 |  | 29967 | Whakaki | Wairoa | Nuhaka 3203 | 2024-12-27 13:59 | 45653.5826 | 2024-12-28 14:58 | 45654.6236 | 1.05 | 0.0017279 | 45 | 27345 | Unplanned | Vegetation | Tree through HV Lines W8134
1019 |  | 29959 | Rototahia | Gisborne | Rototahi 0403 | 2024-12-27 14:06 | 45653.5875 | 2024-12-29 11:58 | 45655.4986 | 3.378 | 0.023423 | 610 | 87973 | Unplanned | Vegetation | Tree thru line @ E2993
1020 |  | 29912 | Mahia | Wairoa | Mahia 3301 | 2024-12-27 14:37 | 45653.609 | 2024-12-28 11:57 | 45654.4979 | 32.9165 | 0.10886 | 2835 | 857245 | Unplanned | Adverse Weather | 33kV Conductor clashing - 1st fault
1021 |  | 29912 | Mahia | Wairoa | Morere 3401 | 2024-12-27 14:37 | 45653.609 | 2024-12-27 21:16 | 45653.8861 | 2.487 | 0.01966 | 512 | 64768 | Unplanned | Adverse Weather | 33kV Conductor clashing - 1st fault
1022 |  | N/A 54 | Kokahu Road | Wairoa | Morere 3401 | 2024-12-27 14:45 | 45653.6146 | 2024-12-28 22:15 | 45654.9271 | 0.58058 | 0.00030718 | 8 | 15120 | Unplanned | Adverse Weather | Line Clash
1023 |  | N/A 55 | Titirangi | Wairoa | Frasertown 3103 | 2024-12-27 14:57 | 45653.6229 | 2024-12-28 19:52 | 45654.8278 | 1.0659 | 0.00061437 | 16 | 27760 | Unplanned | Adverse Weather | High Winds - Tangled conductors
1024 |  | N/A 69 | Manders Road | Gisborne | Waimata 0903 | 2024-12-27 19:35 | 45653.816 | 2024-12-27 22:21 | 45653.9313 | 0.12111 | 0.00072956 | 19 | 3154 | Unplanned | Adverse Weather | High wind suspect conductor clash
1025 |  | 29961 | Waipiro Bay | Gisborne | Inland 0301 | 2024-12-27 19:45 | 45653.8229 | 2024-12-29 13:06 | 45655.5458 | 0.33464 | 0.0026879 | 70 | 8715 | Unplanned | Vegetation | Tree thru line - H2246
1026 |  | N/A 53 | Goodwin Road | Gisborne | Whangara 0506 | 2024-12-27 20:35 | 45653.8576 | 2024-12-28 08:48 | 45654.3667 | 0.42219 | 0.00057597 | 15 | 10995 | Unplanned | Vegetation | Tree on line - Windy
1027 |  | 117247 | 410 Goodwin Road | Gisborne | Whangara 0506 | 2024-12-27 21:01 | 45653.8757 | 2024-12-28 10:00 | 45654.4167 | 0.44868 | 0.00057597 | 15 | 11685 | Unplanned | Vegetation | Replace fuse
1028 |  | N/A 65 | Morere | Wairoa | Morere 3401 | 2024-12-27 21:50 | 45653.9097 | 2024-12-28 10:52 | 45654.4528 | 2.192 | 0.0028031 | 73 | 57086 | Unplanned | Adverse Weather | Suspect clashing - High Winds
1029 |  | 29968 | Mangapoike | Wairoa | Frasertown 3103 | 2024-12-27 23:24 | 45653.975 | 2024-12-28 17:40 | 45654.7361 | 2.7094 | 0.0046846 | 122 | 70562 | Unplanned | Vegetation | Tree thru line check zone - windy
1030 |  | 117451 | 1235 Panikau Road | Gisborne | Rototahi 0403 | 2024-12-28 08:05 | 45654.3368 | 2024-12-28 18:30 | 45654.7708 | 0.21599 | 0.00034558 | 9 | 5625 | Unplanned | Adverse Weather | Replace fuse
1031 |  | 29913 | Mahia East Coast Road | Wairoa | Mahia 3301 | 2024-12-28 09:25 | 45654.3924 | 2024-12-28 10:15 | 45654.4271 | 0.044158 | 0.00088315 | 23 | 1150 | Unplanned | Adverse Weather | Repaired broken LV wires - High wind
1032 |  | 29979 | Rangiahua Road | Wairoa | Frasertown 3103 | 2024-12-28 09:59 | 45654.416 | 2025-01-06 16:16 | 45663.6778 | 0.05514 | 7.6796e-05 | 2 | 1436 | Unplanned | Vegetation | Tree thru line W4064 - High Winds - Install Gen
1033 |  | 29964 | Matawai | Gisborne | Matawai 1204 | 2024-12-28 10:23 | 45654.4326 | 2024-12-28 13:44 | 45654.5722 | 0.65929 | 0.0092155 | 240 | 17170 | Unplanned | Defective Equipment | Failed inline crimp - Windy
1034 |  | 117691 | 758 Glenroy Road | Gisborne | Dalton 0502 | 2024-12-28 10:47 | 45654.4493 | 2024-12-28 17:00 | 45654.7083 | 0.014322 | 3.8398e-05 | 1 | 373 | Unplanned | Adverse Weather | Replace fuse
1035 |  | 118044 | 4513 Rukeliti Road | Gisborne | Inland 0301 | 2024-12-28 15:06 | 45654.6292 | 2024-12-28 17:00 | 45654.7083 | 0.043774 | 0.00038398 | 10 | 1140 | Unplanned | Unknown cause | Replace fuses
1036 |  | 118297 | 401 Titirangi Road | Wairoa | Frasertown 3103 | 2024-12-28 18:25 | 45654.7674 | 2024-12-28 20:25 | 45654.8507 | 0.073724 | 0.00061437 | 16 | 1920 | Unplanned | Unknown cause | Replace fuses
1037 |  | 29972 | Mangaone Road | Wairoa | Morere 3401 | 2024-12-28 18:58 | 45654.7903 | 2024-12-29 20:19 | 45655.8465 | 0.64167 | 0.00042238 | 11 | 16711 | Unplanned | Defective Equipment | Conductor off the insulator & fell on the ground at Pole W8065. Bindings rusted away due to age. The Pole & crossare needs replacemnt in the near future
1038 |  | 29970 | Kaiwaitau Road | Wairoa | Mahia 3301 | 2024-12-28 21:20 | 45654.8889 | 2024-12-28 21:41 | 45654.9035 | 0.0024191 | 0.00011519 | 3 | 63 | Unplanned | Adverse Weather | Blown jumper at TX - High winds
1039 |  | 118630 | 249 Makanga Road | Wairoa | Mahia 3301 | 2024-12-29 08:31 | 45655.3549 | 2024-12-29 10:30 | 45655.4375 | 0.036555 | 0.00030718 | 8 | 952 | Unplanned | Unknown cause | Replace fuses
1040 |  | 118687 | 63 Thomas Rd | Gisborne | Rototahi 0403 | 2024-12-29 09:25 | 45655.3924 | 2024-12-29 10:30 | 45655.4375 | 0.0074876 | 0.00011519 | 3 | 195 | Unplanned | Unknown cause | Replace fuses
1041 |  | 29971 | Mahia | Wairoa | Mahia 3301 | 2024-12-29 11:00 | 45655.4583 | 2024-12-30 17:29 | 45656.7285 | 0.56184 | 0.00030718 | 8 | 14632 | Unplanned | Defective Equipment | Failed insulator, burnt x-arm steel pole. Replaced pole
1042 |  | 118864 | 703 Waiapu Road | Gisborne | Makarika 0204 | 2024-12-29 12:43 | 45655.5299 | 2024-12-29 13:45 | 45655.5729 | 0.011903 | 0.00019199 | 5 | 310 | Unplanned | Unknown cause | Replace fuse
1043 |  | 29975 | Lake Road | Wairoa | Frasertown 3103 | 2024-12-29 15:21 | 45655.6396 | 2025-01-01 14:06 | 45658.5875 | 0.163 | 3.8398e-05 | 1 | 4245 | Unplanned | Lightning | Lightning blew TX
1044 |  | 116988 | 200 Faulkner road | Gisborne | Tahora 1103 | 2024-12-29 17:08 | 45655.7139 | 2024-12-29 19:00 | 45655.7917 | 0.012902 | 0.00011519 | 3 | 336 | Unplanned | Unknown cause | Replace fuse
1045 |  | 29918 | Hereheretau Road | Wairoa | Nuhaka 3203 | 2024-12-29 19:05 | 45655.7951 | 2024-12-30 13:24 | 45656.5583 | 0.42199 | 0.00038398 | 10 | 10990 | Unplanned | Vegetation | Tree on line
1046 |  | N/A 62 | Muriwai Feeder | Gisborne | Muriwai 0905 | 2024-12-30 06:00 | 45656.25 | 2024-12-30 07:06 | 45656.2958 | 1.0467 | 0.015858 | 413 | 27258 | Unplanned | Vegetation | Tree branch across line at Pole C924
1047 |  | 119468 | 593 Waipiro Road | Gisborne | Inland 0301 | 2024-12-30 06:53 | 45656.2868 | 2024-12-30 08:00 | 45656.3333 | 0.051453 | 0.00076796 | 20 | 1340 | Unplanned | Wildlife | Replace fuses
1048 |  | 119965 | Tawera Road | Gisborne | Te Arai 0906 | 2024-12-30 15:56 | 45656.6639 | 2024-12-31 10:30 | 45657.4375 | 0.21388 | 0.00019199 | 5 | 5570 | Unplanned | Vegetation | Replace fuse
1049 |  | 119992 | 846 Erepeti Road | Wairoa | Ruakituri 2003 | 2024-12-30 16:08 | 45656.6722 | 2024-12-30 20:30 | 45656.8542 | 0.060362 | 0.00023039 | 6 | 1572 | Unplanned | Lightning | Replace fuses
1050 |  | 120005 | 338 Tuahau Road | Gisborne | Tauwhareparae 0404 | 2024-12-30 16:29 | 45656.6868 | 2025-01-01 09:00 | 45658.375 | 0.093346 | 3.8398e-05 | 1 | 2431 | Unplanned | Unknown cause | Replace fuse
1051 |  | 120169 | 409 Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2024-12-30 18:43 | 45656.7799 | 2024-12-30 20:00 | 45656.8333 | 0.011827 | 0.00015359 | 4 | 308 | Unplanned | Lightning | Replace fuses
1052 |  | 120300 | 1692 Parikanapa Road | Gisborne | Parikanapa 1002 | 2024-12-30 21:11 | 45656.8826 | 2024-12-31 08:00 | 45657.3333 | 0.049841 | 7.6796e-05 | 2 | 1298 | Unplanned | Lightning | Replace fuse
1053 |  | 120327 | 36 Saddler Road | Gisborne | Te Arai 0906 | 2024-12-30 21:55 | 45656.9132 | 2024-12-31 10:15 | 45657.4271 | 0.028415 | 3.8398e-05 | 1 | 740 | Unplanned | Lightning | Replace fuses
1054 |  | N/A 85 | 213 Taurau Valley Road | Gisborne | Te Arai 0906 | 2024-12-30 22:00 | 45656.9167 | 2024-12-31 10:00 | 45657.4167 | 0.055293 | 7.6796e-05 | 2 | 1440 | Unplanned | Lightning | Replace fuse
1055 |  | N/A 86 | 216 Taurau Valley Road | Gisborne | Te Arai 0906 | 2024-12-30 22:00 | 45656.9167 | 2024-12-31 10:00 | 45657.4167 | 0.027647 | 3.8398e-05 | 1 | 720 | Unplanned | Lightning | Replace fuse
1056 |  | 120478 | 145 Rere Farm Settlement road | Gisborne | Tahora 1103 | 2024-12-31 06:49 | 45657.284 | 2024-12-31 08:10 | 45657.3403 | 0.024882 | 0.00030718 | 8 | 648 | Unplanned | Unknown cause | Replace fuse
1057 |  | 29977 | Matanui Road | Gisborne | Tauwhareparae 0404 | 2024-12-31 07:08 | 45657.2972 | 2025-01-02 20:12 | 45659.8417 | 0.70345 | 0.00019199 | 5 | 18320 | Unplanned | Unknown cause | Check cause
1058 |  | 120501 | 201 Matanui Road | Gisborne | Tauwhareparae 0404 | 2024-12-31 07:08 | 45657.2972 | 2024-12-31 09:00 | 45657.375 | 0.021503 | 0.00019199 | 5 | 560 | Unplanned | Lightning | Replace fuses
1059 |  | 120496 | 1271 Rakaura Road | Gisborne | Matawai 1204 | 2024-12-31 07:10 | 45657.2986 | 2024-12-31 10:00 | 45657.4167 | 0.013055 | 7.6796e-05 | 2 | 340 | Unplanned | Lightning | Replace fuse
1060 |  | 120533 | 49 Makarika Road | Gisborne | Seaside 0302 | 2024-12-31 07:49 | 45657.3257 | 2024-12-31 09:15 | 45657.3854 | 0.016511 | 0.00019199 | 5 | 430 | Unplanned | Lightning | Replace fuse
1061 |  | N/A 57 | Waitangi Road | Gisborne | Kanakanaia 1202 | 2024-12-31 09:25 | 45657.3924 | 2024-12-31 22:57 | 45657.9563 | 0.37415 | 0.00046078 | 12 | 9744 | Unplanned | Vegetation | Tree thru lines - high winds
1062 |  | 120620 | 3276 Te Araroa Road | Gisborne | Awatere 0101 | 2024-12-31 09:39 | 45657.4021 | 2024-12-31 11:45 | 45657.4896 | 0.0048382 | 3.8398e-05 | 1 | 126 | Unplanned | Lightning | Replace fuse
1063 |  | 120630 | 721 Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2024-12-31 09:56 | 45657.4139 | 2024-12-31 11:48 | 45657.4917 | 0.0086012 | 7.6796e-05 | 2 | 224 | Unplanned | Lightning | Replace fuses
1064 |  | 120663 | 1880 East Cape Road | Gisborne | Tiki Tiki 0206 | 2024-12-31 10:40 | 45657.4444 | 2024-12-31 11:40 | 45657.4861 | 0.0046078 | 7.6796e-05 | 2 | 120 | Unplanned | Lightning | Replace fuses
1065 |  | N/A 56 | Tawera Road | Gisborne | Te Arai 0906 | 2024-12-31 10:52 | 45657.4528 | 2024-12-31 12:32 | 45657.5222 | 0.019199 | 0.00019199 | 5 | 500 | Unplanned | Adverse Weather | High Winds - Clashing
1066 |  | 120736 | Thatcher road | Gisborne | Tiki Tiki 0206 | 2024-12-31 12:05 | 45657.5035 | 2024-12-31 13:40 | 45657.5694 | 0.0036478 | 3.8398e-05 | 1 | 95 | Unplanned | Lightning | Replace fuses
1067 |  | 120815 | 112 Onepoto Road | Gisborne | Hicks Bay 0102 | 2024-12-31 13:51 | 45657.5771 | 2024-12-31 14:50 | 45657.6181 | 0.015858 | 0.00026879 | 7 | 413 | Unplanned | Lightning | Replace fuses
1068 |  | 119960 | 327 Heliburton Road | Wairoa | Raupunga 3101 | 2024-12-31 15:35 | 45657.6493 | 2024-12-31 18:10 | 45657.7569 | 0.0059517 | 3.8398e-05 | 1 | 155 | Unplanned | Lightning | Replace fuses
1069 |  | 120946 | 1884 Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2024-12-31 16:07 | 45657.6715 | 2024-12-31 17:20 | 45657.7222 | 0.011212 | 0.00015359 | 4 | 292 | Unplanned | Lightning | Replace fuses
1070 |  | 120955 | 75 Church Lane | Wairoa | Raupunga 3101 | 2024-12-31 16:35 | 45657.691 | 2024-12-31 17:30 | 45657.7292 | 0.0042238 | 7.6796e-05 | 2 | 110 | Unplanned | Lightning | Replace fuse
1071 |  | N/A 63 | North Clyde / McLean St / Tawhara Valley | Wairoa | Brickworks 3201 | 2024-12-31 17:26 | 45657.7264 | 2024-12-31 18:44 | 45657.7806 | 1.6832 | 0.023692 | 617 | 43836 | Unplanned | Adverse Weather | Suspect Wind Clash @ sewage plant
1072 |  | 120101 | 473 Hiririroa Road | Gisborne | Totangi 1101 | 2024-12-31 17:58 | 45657.7486 | 2024-12-31 19:00 | 45657.7917 | 0.0047614 | 7.6796e-05 | 2 | 124 | Unplanned | Lightning | Replace fuses
1073 |  | 120673 | 1005 Hiririroa Road | Gisborne | Totangi 1101 | 2024-12-31 18:31 | 45657.7715 | 2024-12-31 19:30 | 45657.8125 | 0.0022655 | 3.8398e-05 | 1 | 59 | Unplanned | Unknown cause | Replace fuses
1074 |  | 29976 | Ihungia Road | Gisborne | Mata 0304 | 2024-12-31 18:48 | 45657.7833 | 2025-01-01 13:19 | 45658.5549 | 0.5355 | 0.00061437 | 16 | 13946 | Unplanned | Vegetation | Tree fell over line
1075 |  | N/A 58 | Kaiti | Gisborne | Kaiti Sub 05 | 2024-12-31 19:16 | 45657.8028 | 2024-12-31 19:45 | 45657.8229 | 0.0011135 | 3.8398e-05 | 1 | 29 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over
1076 |  | N/A 58 | Kaiti | Gisborne | Herschell 0501 | 2024-12-31 19:16 | 45657.8028 | 2024-12-31 19:45 | 45657.8229 | 0.19598 | 0.0067581 | 176 | 5104 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over
1077 |  | N/A 58 | Kaiti | Gisborne | Dalton 0502 | 2024-12-31 19:16 | 45657.8028 | 2024-12-31 19:45 | 45657.8229 | 0.91422 | 0.031525 | 821 | 23809 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over
1078 |  | N/A 58 | Kaiti | Gisborne | Tamarau 0503 | 2024-12-31 19:16 | 45657.8028 | 2024-12-31 19:45 | 45657.8229 | 1.177 | 0.040587 | 1057 | 30653 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over
1079 |  | N/A 58 | Kaiti | Gisborne | Wainui 0504 | 2024-12-31 19:16 | 45657.8028 | 2024-12-31 19:45 | 45657.8229 | 0.72603 | 0.025036 | 652 | 18908 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over
1080 |  | N/A 58 | Kaiti | Gisborne | Whangara 0506 | 2024-12-31 19:16 | 45657.8028 | 2024-12-31 19:45 | 45657.8229 | 0.65588 | 0.022616 | 589 | 17081 | Unplanned | Vegetation | Tree @ B5038. Heavy rain & Wind, Flash over
1081 |  | 29973 | Tiniroto road | Gisborne | Tiniroto 1003 | 2024-12-31 19:27 | 45657.8104 | 2024-12-31 23:58 | 45657.9986 | 0.44907 | 0.0032638 | 85 | 11695 | Unplanned | Vegetation | Tree thru line D386 - High Winds
1082 |  | 120225 | 4029 Tauwhareparae Rd | Gisborne | Tauwhareparae 0404 | 2024-12-31 19:49 | 45657.8257 | 2025-01-01 10:00 | 45658.4167 | 0.065353 | 7.6796e-05 | 2 | 1702 | Unplanned | Defective Equipment | Replacr fuses & wire
1083 |  | 120249 | 91 Marumoko Road | Gisborne | Matawai 1204 | 2024-12-31 19:59 | 45657.8326 | 2024-12-31 21:00 | 45657.875 | 0.0023423 | 3.8398e-05 | 1 | 61 | Unplanned | Lightning | Replace fuse
1084 |  | 120315 | 899 Poroporo Road | Gisborne | Tiki Tiki 0206 | 2024-12-31 21:30 | 45657.8958 | 2024-12-31 23:00 | 45657.9583 | 0.044926 | 0.00049917 | 13 | 1170 | Unplanned | Lightning | Replace fuses
1085 |  | 121468 | 5591 Matawai Road | Gisborne | Mata 0304 | 2025-01-01 08:48 | 45658.3667 | 2025-01-01 09:20 | 45658.3889 | 0.0012287 | 3.8398e-05 | 1 | 32 | Unplanned | Lightning | Replace fuse
1086 |  | 121577 | 4539 Te Araroa Road | Gisborne | Hicks Bay 0102 | 2025-01-01 11:31 | 45658.4799 | 2025-01-01 14:15 | 45658.5938 | 0.0062973 | 3.8398e-05 | 1 | 164 | Unplanned | Lightning | Replace fuses
1087 |  | 121605 | 146 Matanui Road | Gisborne | Tauwhareparae 0404 | 2025-01-01 12:22 | 45658.5153 | 2025-01-02 08:00 | 45659.3333 | 0.045233 | 3.8398e-05 | 1 | 1178 | Unplanned | Unknown cause | Replace fuse
1088 |  | 121670 | 481 Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2025-01-01 13:24 | 45658.5583 | 2025-01-01 14:30 | 45658.6042 | 0.0025343 | 3.8398e-05 | 1 | 66 | Unplanned | Lightning | Replace fusewire
1089 |  | 120896 | Onenui Station | Wairoa | Mahia 3301 | 2025-01-01 14:54 | 45658.6208 | 2025-01-01 16:30 | 45658.6875 | 0.0073724 | 7.6796e-05 | 2 | 192 | Unplanned | Lightning | Replace fuse
1090 |  | 29919 | Tiniroto | Gisborne | Tiniroto 1003 | 2025-01-02 08:27 | 45659.3521 | 2025-01-02 15:24 | 45659.6417 | 0.5959 | 0.004531 | 118 | 15519 | Unplanned | Vegetation | Tree through the line at D3289
1091 |  | 29922 | Hikuwai | Gisborne | Mata 0304 | 2025-01-02 11:43 | 45659.4882 | 2025-01-02 17:10 | 45659.7153 | 0.37292 | 0.0032638 | 85 | 9712 | Unplanned | Vegetation | Tree across the line @ H714
1092 |  | N/A 66 | Kahunganga | Wairoa | Raupunga 3101 | 2025-01-02 13:20 | 45659.5556 | 2025-01-02 17:58 | 45659.7486 | 0.20865 | 0.00095995 | 25 | 5434 | Unplanned | Adverse Weather | High winds causing trees to clash conductor
1093 |  | 29924 | Tahora | Gisborne | Matawai 1204 | 2025-01-02 14:07 | 45659.5882 | 2025-01-04 11:58 | 45661.4986 | 0.3169 | 0.00011519 | 3 | 8253 | Unplanned | Lightning | Lightnening blew TX
1094 |  | 123326 | 8 Judd Road | Gisborne | Lavenham 0902 | 2025-01-03 14:52 | 45660.6194 | 2025-01-03 16:00 | 45660.6667 | 0.013055 | 0.00019199 | 5 | 340 | Unplanned | Unknown cause | Replace fuse
1095 |  | 122848 | 350 Erepeti Rd | Wairoa | Ruakituri 2003 | 2025-01-03 19:15 | 45660.8021 | 2025-01-03 20:30 | 45660.8542 | 0.0028799 | 3.8398e-05 | 1 | 75 | Unplanned | Unknown cause | Replace fuse
1096 |  | 122844 | 404 Armstrong Road | Gisborne | Whatatutu 1201 | 2025-01-03 19:19 | 45660.8049 | 2025-01-03 20:55 | 45660.8715 | 0.0036862 | 3.8398e-05 | 1 | 96 | Unplanned | Unknown cause | Replace fuse
1097 |  | 123742 | 1341 Mahia Settlement Road | Wairoa | Mahia 3301 | 2025-01-04 07:45 | 45661.3229 | 2025-01-04 09:45 | 45661.4062 | 0.04147 | 0.00034558 | 9 | 1080 | Unplanned | Lightning | Replace fuses
1098 |  | 123772 | 4988 Te Araroa Road | Gisborne | Hicks Bay 0102 | 2025-01-04 08:05 | 45661.3368 | 2025-01-04 10:00 | 45661.4167 | 0.013247 | 0.00011519 | 3 | 345 | Unplanned | Unknown cause | Replace fuse
1099 |  | 29984 | Ruakitori | Wairoa | Ruakituri 2003 | 2025-01-04 12:07 | 45661.5049 | 2025-01-10 12:53 | 45667.5368 | 0.33806 | 0.00015359 | 4 | 8804 | Unplanned | Vegetation | High wind tree thru line
1100 |  | 124086 | 1945 Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2025-01-04 13:32 | 45661.5639 | 2025-01-04 14:55 | 45661.6215 | 0.003187 | 3.8398e-05 | 1 | 83 | Unplanned | Unknown cause | Replace fuse
1101 |  | 29925 | Mahia | Wairoa | Mahia 3301 | 2025-01-04 16:01 | 45661.6674 | 2025-01-04 21:09 | 45661.8812 | 2.1516 | 0.073571 | 1916 | 56033 | Unplanned | Adverse Weather | Indication showed loss of phase, found jumper off arm W8783. High Winds use generator, High Winds Clashing
1102 |  | 29926 | Whatatutu | Gisborne | Whatatutu 1201 | 2025-01-04 17:59 | 45661.7493 | 2025-01-04 23:40 | 45661.9861 | 0.72538 | 0.0048382 | 126 | 18891 | Unplanned | Adverse Weather | Wires down at pole E714 - High Winds
1103 |  | 29927 | 6590 Waiapu Road | Gisborne | Makarika 0204 | 2025-01-05 13:58 | 45662.5819 | 2025-01-06 12:08 | 45663.5056 | 0.15674 | 0.0028031 | 73 | 4082 | Unplanned | Lightning | Suspected Lightning strike
1104 |  | 125577 | 701 Tapuaeroa Rd | Gisborne | Tiki Tiki 0206 | 2025-01-05 21:53 | 45662.9118 | 2025-01-06 10:53 | 45663.4535 | 0.059901 | 7.6796e-05 | 2 | 1560 | Unplanned | Lightning | Replace fuses
1105 |  | 29930 | Ruakaka Road | Gisborne | Tiniroto 1003 | 2025-01-06 09:57 | 45663.4146 | 2025-01-06 18:04 | 45663.7528 | 0.15977 | 0.00088315 | 23 | 4161 | Unplanned | Defective Equipment | Faulty TX
1106 |  | 125694 | 55A Waititi Road | Wairoa | Morere 3401 | 2025-01-06 13:14 | 45663.5514 | 2025-01-06 15:00 | 45663.625 | 0.016281 | 0.00015359 | 4 | 424 | Unplanned | Unknown cause | Replace fuse
1107 |  | 29980 | Awapuni Road | Gisborne | Awapuni 0606 | 2025-01-06 15:40 | 45663.6528 | 2025-01-06 15:51 | 45663.6604 | 0.12875 | 0.013439 | 350 | 3353 | Unplanned | Human Error | 2 x feeder tripped whilst parralling, for planned switching
1108 |  | N/A 64 | Ihungia Road | Gisborne | Mata 0304 | 2025-01-07 00:46 | 45664.0319 | 2025-01-07 01:44 | 45664.0722 | 0.035633 | 0.00061437 | 16 | 928 | Unplanned | Unknown cause | Unknown
1109 |  | 29931 | SH2 Waihua Mohaka | Wairoa | Raupunga 3101 | 2025-01-07 01:28 | 45664.0611 | 2025-01-07 11:38 | 45664.4847 | 4.65 | 0.013247 | 345 | 121099 | Unplanned | Adverse Environment | Pine tree thru line W6346 - W1195. All 3 wires (out of zone)
1110 |  | 126286 | 4876 Tiniroto Road | Gisborne | Tiniroto 1003 | 2025-01-07 11:39 | 45664.4854 | 2025-01-08 10:08 | 45665.4222 | 0.051799 | 3.8398e-05 | 1 | 1349 | Unplanned | Unknown cause | Replace fuses
1111 |  | 126324 | Matanui Rd 1km W/Shed + Quarters | Gisborne | Tauwhareparae 0404 | 2025-01-07 15:48 | 45664.6583 | 2025-01-07 17:35 | 45664.7326 | 0.0082172 | 7.6796e-05 | 2 | 214 | Unplanned | Lightning | Been out since lightning
1112 |  | 126712 | 158 Waihau Road | Gisborne | Rototahi 0403 | 2025-01-08 06:31 | 45665.2715 | 2025-01-08 23:15 | 45665.9688 | 0.11565 | 0.00011519 | 3 | 3012 | Unplanned | Lightning | Lightning early hrs. Also birds nestat TX A849
1113 |  | N/A 65a | Tolaga Bay | Gisborne | Tolaga Bay Sub | 2025-01-10 23:56 | 45667.9972 | 2025-01-11 00:30 | 45668.0208 | 0.0013055 | 3.8398e-05 | 1 | 34 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line.
1114 |  | N/A 65a | Tolaga Bay | Gisborne | Toko Tie 0401 | 2025-01-10 23:56 | 45667.9972 | 2025-01-11 00:30 | 45668.0208 | 0.10966 | 0.0032254 | 84 | 2856 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line.
1115 |  | N/A 65a | Tolaga Bay | Gisborne | Town 0402 | 2025-01-10 23:56 | 45667.9972 | 2025-01-11 00:30 | 45668.0208 | 0.26763 | 0.0078716 | 205 | 6970 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line.
1116 |  | N/A 65a | Tolaga Bay | Gisborne | Rototahi 0403 | 2025-01-10 23:56 | 45667.9972 | 2025-01-11 00:30 | 45668.0208 | 0.282 | 0.008294 | 216 | 7344 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line.
1117 |  | N/A 65a | Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2025-01-10 23:56 | 45667.9972 | 2025-01-11 00:30 | 45668.0208 | 0.19061 | 0.0056061 | 146 | 4964 | Unplanned | Unknown cause | Patrol nothing found E/F. Fault indicator didn't detect fault, therefore fault in first part of line.
1118 |  | 128338 | 4314 Ihungia Road | Gisborne | Mata 0304 | 2025-01-11 06:59 | 45668.291 | 2025-01-11 09:10 | 45668.3819 | 0.020121 | 0.00015359 | 4 | 524 | Unplanned | Unknown cause | Replace fuses
1119 |  | 30000 | Harris Street | Gisborne | Harris 1502 | 2025-01-11 12:49 | 45668.534 | 2025-01-13 17:26 | 45670.7264 | 0.94751 | 0.0047614 | 124 | 24676 | Unplanned | Defective Equipment | GM TX caught on fire. Internal fault. Install generator
1120 |  | 129026 | Lake Rd, Patutahi | Gisborne | Lavenham 0902 | 2025-01-12 08:57 | 45669.3729 | 2025-01-12 11:00 | 45669.4583 | 0.028338 | 0.00023039 | 6 | 738 | Unplanned | Wildlife | Replace fuses
1121 |  | 129623 | 6239 Matawai Road | Gisborne | Matawai 1204 | 2025-01-13 06:41 | 45670.2785 | 2025-01-13 09:05 | 45670.3785 | 0.016588 | 0.00011519 | 3 | 432 | Unplanned | Unknown cause | Replace fuse
1122 |  | 129631 | 3 Bond road | Gisborne | Waimata 0903 | 2025-01-13 06:55 | 45670.2882 | 2025-01-13 08:05 | 45670.3368 | 0.053757 | 0.00076796 | 20 | 1400 | Unplanned | Unknown cause | Replace fuse
1123 |  | 129699 | 12.5km Tapuaeroa Rd | Gisborne | Tiki Tiki 0206 | 2025-01-13 08:10 | 45670.3403 | 2025-01-13 10:15 | 45670.4271 | 0.0047998 | 3.8398e-05 | 1 | 125 | Unplanned | Lightning | Apparently been off since lightning
1124 |  | 129694 | 457 Woodlands Road | Wairoa | Raupunga 3101 | 2025-01-13 08:37 | 45670.359 | 2025-01-13 10:55 | 45670.4549 | 0.015897 | 0.00011519 | 3 | 414 | Unplanned | Unknown cause | Replace fuses
1125 |  | 3480 | Christopher Rd / Pa Road | Gisborne | Dalton 0502 | 2025-01-14 09:03 | 45671.3771 | 2025-01-14 16:07 | 45671.6715 | 1.4164 | 0.0033406 | 87 | 15581.3783 | Planned | Planned | Replace 50kV pole A1054
1126 |  | 3458 | Bushmere Road | Gisborne | Waimata 0903 | 2025-01-14 09:05 | 45671.3785 | 2025-01-14 13:47 | 45671.5743 | 0.40065 | 0.0014207 | 37 | 5225.6735 | Planned | Planned | Replace ABS 495
1127 |  | 30657 | Frasertown | Wairoa | Frasertown 3103 | 2025-01-15 06:00 | 45672.25 | 2025-01-15 10:16 | 45672.4278 | 2.584 | 0.025419 | 662 | 67296 | Unplanned | Wildlife | Duck hit/broken line W979 - W813
1128 |  | 3460 | Wellington Street | Gisborne | Childers 0605 | 2025-01-15 09:03 | 45672.3771 | 2025-01-15 09:29 | 45672.3951 | 0.088853 | 0.0034174 | 89 | 1160.954 | Planned | Planned | Replace 11kV Cable stand-off
1129 |  | 130988 | Andrews Road, Whangara | Gisborne | Dalton 0502 | 2025-01-15 09:06 | 45672.3792 | 2025-01-15 12:25 | 45672.5174 | 0.022924 | 0.00011519 | 3 | 597 | Unplanned | Wildlife | Fuse tube also burnt had to replace
1130 |  | 3459 | Aberdeen road | Gisborne | Gladstone 0607 | 2025-01-15 11:02 | 45672.4597 | 2025-01-15 11:50 | 45672.4931 | 0.13455 | 0.0028031 | 73 | 1756.911 | Planned | Planned | Replace 11kV cable stand-off
1131 |  | 131027 | 197 Archillies Street | Wairoa | Borough Two 3205 | 2025-01-15 11:05 | 45672.4618 | 2025-01-15 13:10 | 45672.5486 | 0.047998 | 0.00038398 | 10 | 1250 | Unplanned | Unknown cause | Replace fuse
1132 |  | 3461 | Chalmers Road | Gisborne | Chalmers 0707 | 2025-01-15 13:05 | 45672.5451 | 2025-01-15 13:36 | 45672.5667 | 0.11189 | 0.0036094 | 94 | 1462.2589 | Planned | Planned | Replace 11kV crucitix standoffs
1133 |  | 3462 | Main Rd, Makaraka | Gisborne | Campion 0802 | 2025-01-15 14:31 | 45672.6049 | 2025-01-15 14:50 | 45672.6181 | 0.039396 | 0.0020735 | 54 | 514.0637 | Planned | Planned | Replace 11kV cable stand-offs
1134 |  | 30659 | Wainui Rd | Gisborne | Dalton 0502 | 2025-01-16 05:39 | 45673.2354 | 2025-01-16 07:45 | 45673.3229 | 0.60408 | 0.010598 | 276 | 15732 | Unplanned | Adverse Environment | Salt buildup on ABS A2188 which caused tracking
1135 |  | 3463 | Kiore Road | Gisborne | Tauwhareparae 0404 | 2025-01-16 09:02 | 45673.3764 | 2025-01-16 12:38 | 45673.5264 | 0.066352 | 0.00030718 | 8 | 864.2949 | Planned | Planned | Replace pole G1522
1136 |  | 131730 | 165 Glendening Road | Wairoa | Raupunga 3101 | 2025-01-16 16:45 | 45673.6979 | 2025-01-16 18:50 | 45673.7847 | 0.043198 | 0.00034558 | 9 | 1125 | Unplanned | Unknown cause | Replace fuses
1137 |  | 131755 | 459 Waiomatatini Road | Gisborne | Ruatoria 0201 | 2025-01-16 17:31 | 45673.7299 | 2025-01-16 18:48 | 45673.7833 | 0.041393 | 0.00053757 | 14 | 1078 | Unplanned | Vegetation | Multiple branches near 11kvnear pole J1688
1138 |  | 131813 | 168 Karaua Road | Gisborne | Muriwai 0905 | 2025-01-16 18:25 | 45673.7674 | 2025-01-16 20:30 | 45673.8542 | 0.014399 | 0.00011519 | 3 | 375 | Unplanned | Unknown cause | Replace fuse
1139 |  | 3473 A | Cambridge Tce | Gisborne | Crawford 1504 | 2025-01-17 08:38 | 45674.3597 | 2025-01-17 09:43 | 45674.4049 | 0.22463 | 0.0034558 | 90 | 2935.1083 | Planned | Planned | Replace 11kV cable standoff insulators
1140 |  | 3497 | Waimata Valley Rd / Manders Road | Gisborne | Waimata 0903 | 2025-01-17 09:03 | 45674.3771 | 2025-01-17 10:51 | 45674.4521 | 0.1327 | 0.0012287 | 32 | 3456 | Planned | Planned | To make repairs @ Pole E1168 - Urgent Work
1141 |  | 3472 | Tuparoa road | Gisborne | Ruatoria 0201 | 2025-01-17 09:10 | 45674.3819 | 2025-01-17 12:35 | 45674.5243 | 0.15743 | 0.00076796 | 20 | 2051.5743 | Planned | Planned | Install 2ph 30kVA TX J1591
1142 |  | 3475 | Ranfurly Street | Gisborne | Crawford 1504 | 2025-01-17 10:32 | 45674.4389 | 2025-01-17 11:15 | 45674.4688 | 0.20639 | 0.0047998 | 125 | 2700.3993 | Planned | Planned | Replace 11kV cable standoff insulators
1143 |  | 3474 | Owen Road | Gisborne | Crawford 1504 | 2025-01-17 12:36 | 45674.525 | 2025-01-17 13:23 | 45674.5576 | 0.1534 | 0.0032638 | 85 | 2004.0195 | Planned | Planned | Replace HV cable stand-offs
1144 |  | 132342 | 225 Maclaurin Road | Gisborne | Haisman 0804 | 2025-01-17 16:18 | 45674.6792 | 2025-01-17 18:20 | 45674.7639 | 0.0093691 | 7.6796e-05 | 2 | 244 | Unplanned | Unknown cause | Replace fuse
1145 |  | 133618 | 204 Pa Rd | Gisborne | Dalton 0502 | 2025-01-19 10:13 | 45676.4257 | 2025-01-19 12:20 | 45676.5139 | 0.13654 | 0.0010751 | 28 | 3556 | Unplanned | Unknown cause | Replace fuse
1146 |  | 3478 | Wharekopae Road | Gisborne | Tahunga 1004 | 2025-01-20 15:01 | 45677.6257 | 2025-01-20 16:16 | 45677.6778 | 0.15021 | 0.0030718 | 80 | 1958.1712 | Planned | Planned | To connect generator. Phase rotation incorrect required subsequant outage.
1147 |  | 134449 | Waiomatatini Road | Gisborne | Ruatoria 0201 | 2025-01-20 16:28 | 45677.6861 | 2025-01-20 18:54 | 45677.7875 | 0.078486 | 0.00053757 | 14 | 2044 | Unplanned | Defective Equipment | Replace fuses
1148 |  | 30717 | Waiomatatini Road | Gisborne | Ruatoria 0201 | 2025-01-20 18:24 | 45677.7667 | 2025-01-20 18:57 | 45677.7896 | 0.01774 | 0.00053757 | 14 | 462 | Unplanned | Defective Equipment | Temporary restrain of conductor to provide clearance from LV underbuilt. Shackle pulled out.
1149 |  | 3477 | Somerton Road | Gisborne | Haisman 0804 | 2025-01-21 08:03 | 45678.3354 | 2025-01-21 15:14 | 45678.6347 | 0.38064 | 0.00088315 | 23 | 4960.8774 | Planned | Planned | Cut trees
1150 |  | 134949 | 653 Mangapoiki Road | Wairoa | Frasertown 3103 | 2025-01-21 08:58 | 45678.3736 | 2025-01-21 10:00 | 45678.4167 | 0.0047614 | 7.6796e-05 | 2 | 124 | Unplanned | Unknown cause | Replace fuse
1151 |  | 3479 | Wharekopare Road | Gisborne | Tahora 1103 | 2025-01-22 12:30 | 45679.5208 | 2025-01-22 13:13 | 45679.5507 | 0.092462 | 0.0021503 | 56 | 0 | Planned | Planned | To disconnect and remove 300kVA Gen Truck at pole D5035
1152 |  | 3485 | Riverside Road | Gisborne | Whangara 0506 | 2025-01-23 08:55 | 45680.3715 | 2025-01-23 13:41 | 45680.5701 | 0.043927 | 0.00015359 | 4 | 572.1106 | Planned | Planned | Realign o/head 11kV line. Install 3 x new poles
1153 |  | 136307 | 113 Riuohangi Road | Wairoa | Frasertown 3103 | 2025-01-23 18:28 | 45680.7694 | 2025-01-23 19:30 | 45680.8125 | 0.014284 | 0.00023039 | 6 | 372 | Unplanned | Unknown cause | Replace fuse
1154 |  | 136682 | 127 Blucks Pit | Wairoa | Morere 3401 | 2025-01-24 08:22 | 45681.3486 | 2025-01-24 10:20 | 45681.4306 | 0.0090619 | 7.6796e-05 | 2 | 236 | Unplanned | Unknown cause | Replace fuses
1155 |  | 3508 | Waiomatatini | Gisborne | Ruatoria 0201 | 2025-01-24 09:01 | 45681.3757 | 2025-01-24 12:13 | 45681.509 | 0.10321 | 0.00053757 | 14 | 2688 | Planned | Planned | Urgent Work to replace faulty pole
1156 |  | 3507 | Mitchell Rd/ Churchill Ave | Wairoa | Borough Two 3205 | 2025-01-24 09:02 | 45681.3764 | 2025-01-24 10:36 | 45681.4417 | 0.36455 | 0.0038782 | 101 | 9494 | Planned | Planned | Urgent Work to repair pulled out insulator
1157 |  | 3446 | Ngakaroa Road | Gisborne | Waimata 0903 | 2025-01-24 09:03 | 45681.3771 | 2025-01-24 16:15 | 45681.6771 | 0.36493 | 0.00084476 | 22 | 4590.8749 | Planned | Planned | Tree cutting
1158 |  | 30671 | Otoi road | Wairoa | Raupunga 3101 | 2025-01-24 12:11 | 45681.5076 | 2025-01-24 13:28 | 45681.5611 | 0.03548 | 0.00046078 | 12 | 924 | Unplanned | Defective Equipment | Cracked at HV insulator on pole W5064
1159 |  | 138449 | Tahora settlement Rd | Gisborne | Tahora 1103 | 2025-01-26 16:09 | 45683.6729 | 2025-01-26 17:30 | 45683.7292 | 0.018661 | 0.00023039 | 6 | 486 | Unplanned | Unknown cause | Replace fuse
1160 |  | 138931 | Nuhaka River Road | Wairoa | Morere 3401 | 2025-01-27 10:51 | 45684.4521 | 2025-01-27 12:20 | 45684.5139 | 0.0068349 | 7.6796e-05 | 2 | 178 | Unplanned | Unknown cause | Replace fuses
1161 |  | 139073 | 362 Whakaangiangi Rd | Gisborne | Awatere 0101 | 2025-01-27 14:26 | 45684.6014 | 2025-01-29 15:11 | 45686.6326 | 0.11231 | 3.8398e-05 | 1 | 2925 | Unplanned | Defective Equipment | 1xddo kept blowing. Without lv fuses in also. Will need TX + DDO's replaced. Ancient
1162 |  | 30677 | Tiniroto road | Wairoa | Frasertown 3103 | 2025-01-27 16:02 | 45684.6681 | 2025-01-27 20:15 | 45684.8438 | 0.34696 | 0.0029183 | 76 | 9036 | Unplanned | Vegetation | Tree fallen across lines
1163 |  | 139223 | 404 Armstrong Road | Gisborne | Whatatutu 1201 | 2025-01-27 18:41 | 45684.7785 | 2025-01-27 20:40 | 45684.8611 | 0.0045694 | 3.8398e-05 | 1 | 119 | Unplanned | Vegetation | Replace fuse
1164 |  | 139259 | 2253 Te Araroa Road | Gisborne | Awatere 0101 | 2025-01-27 18:56 | 45684.7889 | 2025-01-27 20:30 | 45684.8542 | 0.010828 | 0.00011519 | 3 | 282 | Unplanned | Adverse Weather | Replace fuses
1165 |  | 139532 | 454 Tauwhareparae Rd, Mangaheia stn | Gisborne | Tauwhareparae 0404 | 2025-01-28 08:47 | 45685.366 | 2025-01-28 10:45 | 45685.4479 | 0.004531 | 3.8398e-05 | 1 | 118 | Unplanned | Adverse Weather | Replace fuse
1166 |  | 30722 | Whakaangiangi Road | Gisborne | Awatere 0101 | 2025-01-28 11:53 | 45685.4951 | 2025-01-28 12:55 | 45685.5382 | 0.038091 | 0.00061437 | 16 | 992 | Unplanned | Lightning | Replace TX J324
1167 |  | 140110 | 27 Marumoko Road | Gisborne | Matawai 1204 | 2025-01-29 08:00 | 45686.3333 | 2025-01-29 10:00 | 45686.4167 | 0.22117 | 0.0018431 | 48 | 5760 | Unplanned | Unknown cause | Replace fuse
1168 |  | 3482 | Hikuwai Drive | Gisborne | Mata 0304 | 2025-01-29 08:34 | 45686.3569 | 2025-01-29 16:32 | 45686.6889 | 0.018354 | 3.8398e-05 | 1 | 239.0092 | Planned | Planned | Replace 50kV poles
1169 |  | 3483 | Waiapu Road | Gisborne | Mata 0304 | 2025-01-30 08:34 | 45687.3569 | 2025-01-30 15:10 | 45687.6319 | 0.015206 | 3.8398e-05 | 1 | 198.0076 | Planned | Planned | 11kV isolated for safety. Replace 50kV pole H1158
1170 |  | 140733 | Makarika / Karewa cnr | Gisborne | Makarika 0204 | 2025-01-30 08:54 | 45687.3708 | 2025-01-30 10:15 | 45687.4271 | 0.012441 | 0.00015359 | 4 | 324 | Unplanned | Wildlife | Line patrol completed. Lots of ducks/geese in paddocks
1171 |  | 3490 | 1900 Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2025-01-30 12:28 | 45687.5194 | 2025-01-30 14:59 | 45687.6243 | 0.023192 | 0.00015359 | 4 | 244.0375 | Planned | Planned | Replace TX J35
1172 |  | 3496 | 1900 Te Araroa Road | Gisborne | Hicks Bay 0102 | 2025-01-31 08:00 | 45688.3333 | 2025-01-31 12:14 | 45688.5097 | 2.5456 | 0.010022 | 261 | 23725.4141 | Planned | Planned | Install new HV links @ J596 & associated s/gear
1173 |  | 3488c | Tuai | Wairoa | Ruakituri 2003 | 2025-01-31 09:06 | 45688.3792 | 2025-01-31 17:46 | 45688.7403 | 3.2516 | 0.0062589 | 163 | 36277.8671 | Planned | Planned | Tuai Sub 5yr maintenance
1174 |  | 3488a | Tuai | Wairoa | Lake | 2025-01-31 09:23 | 45688.391 | 2025-01-31 10:11 | 45688.4243 | 0.0042238 | 0.0011519 | 30 | 0 | Planned | Planned | Tuai Sub 5yr maintenance
1175 |  | 3488a | Tuai | Wairoa | Village 2002 | 2025-01-31 09:23 | 45688.391 | 2025-01-31 10:11 | 45688.4243 | 0.073916 | 0.020159 | 525 | 0 | Planned | Planned | Tuai Sub 5yr maintenance
1176 |  | N/A 67 | All Tuai Sub | Wairoa | Tuai-Wairoa A 5004 | 2025-01-31 12:36 | 45688.525 | 2025-01-31 12:46 | 45688.5319 | 0.13478 | 0.013478 | 351 | 3510 | Unplanned | Human Error | Switch CB's over for MTC
1177 |  | 3488b | Tuai | Wairoa | Lake | 2025-01-31 17:37 | 45688.734 | 2025-01-31 17:44 | 45688.7389 | 0.0026879 | 0.00038398 | 10 | 0 | Planned | Planned | Tuai Sub 5yr maintenance
1178 |  | 3488b | Tuai | Wairoa | Village 2002 | 2025-01-31 17:37 | 45688.734 | 2025-01-31 17:44 | 45688.7389 | 0.047038 | 0.0067197 | 175 | 0 | Planned | Planned | Tuai Sub 5yr maintenance
1179 |  | 142593 | 1226 Mangapoike Road | Wairoa | Frasertown 3103 | 2025-02-01 17:55 | 45689.7465 | 2025-02-01 18:30 | 45689.7708 | 0.0026879 | 7.6796e-05 | 2 | 70 | Unplanned | Unknown cause | Replace fuses
1180 |  | 142675 | 4029 Tauwhareparae Rd | Gisborne | Tauwhareparae 0404 | 2025-02-01 20:00 | 45689.8333 | 2025-02-02 08:35 | 45690.3576 | 0.057981 | 7.6796e-05 | 2 | 1510 | Unplanned | Lightning | Replace fuses
1181 |  | N/A 68 | Tiniroto Rd, Ruakaka Road | Gisborne | Tiniroto 1003 | 2025-02-01 21:25 | 45689.8924 | 2025-02-02 08:45 | 45690.3646 | 0.51768 | 0.0057597 | 150 | 13482 | Unplanned | Wildlife | Possum at pole D3559. Pole has possum guard, may have climbed via stay wire.
1182 |  | 142830 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-02-02 06:30 | 45690.2708 | 2025-02-02 08:15 | 45690.3438 | 0.024191 | 0.00023039 | 6 | 630 | Unplanned | Lightning | Replace fuses
1183 |  | 142833 | 213 Taurau Valley Road | Gisborne | Te Arai 0906 | 2025-02-02 06:36 | 45690.275 | 2025-02-02 09:15 | 45690.3854 | 0.012211 | 7.6796e-05 | 2 | 318 | Unplanned | Lightning | Replace fuse
1184 |  | 30691 | Wharerata Road | Gisborne | Muriwai 0905 | 2025-02-02 06:45 | 45690.2812 | 2025-02-12 10:27 | 45700.4354 | 0.56146 | 3.8398e-05 | 1 | 14622 | Unplanned | Lightning | Replace TX C394 - Power not needed, no access
1185 |  | 3499 | Bright Street | Gisborne | City 0602 | 2025-02-02 07:39 | 45690.3187 | 2025-02-02 13:45 | 45690.5729 | 0.084322 | 0.00023039 | 6 | 1098.3732 | Planned | Planned | To replace RMU B1047, B510, B511, B512
1186 |  | 142881 | 564 Centennial Marine Drive | Gisborne | JNL_A 1405 | 2025-02-02 08:28 | 45690.3528 | 2025-02-02 09:00 | 45690.375 | 0.0086012 | 0.00026879 | 7 | 224 | Unplanned | Unknown cause | Replace fuse
1187 |  | 142951 | 36 Saddler Road | Gisborne | Te Arai 0906 | 2025-02-02 10:09 | 45690.4229 | 2025-02-02 11:30 | 45690.4792 | 0.0031102 | 3.8398e-05 | 1 | 81 | Unplanned | Lightning | Replace fuses
1188 |  | 30746 | Matanui Road | Gisborne | Tauwhareparae 0404 | 2025-02-02 12:30 | 45690.5208 | 2025-02-03 12:21 | 45691.5146 | 0.1099 | 7.6796e-05 | 2 | 2862 | Unplanned | Lightning | Replaced TX G233
1189 |  | 143354 | 708 Mahunga Road | Wairoa | Mahia 3301 | 2025-02-02 20:04 | 45690.8361 | 2025-02-03 09:00 | 45691.375 | 0.14898 | 0.00019199 | 5 | 3880 | Unplanned | Unknown cause | Replace fuses
1190 |  | 143631 | 4988 Te Araroa Road | Gisborne | Hicks Bay 0102 | 2025-02-03 11:28 | 45691.4778 | 2025-02-03 13:30 | 45691.5625 | 0.014054 | 0.00011519 | 3 | 366 | Unplanned | Unknown cause | Replace fuse
1191 |  | 143739 | 1435 Waingake Road | Gisborne | Te Arai 0906 | 2025-02-03 15:27 | 45691.6438 | 2025-02-03 17:33 | 45691.7312 | 0.0096763 | 7.6796e-05 | 2 | 252 | Unplanned | Lightning | Replace fuse
1192 |  | 143360 | 1116 Motu Road | Gisborne | Matawai 1204 | 2025-02-03 19:35 | 45691.816 | 2025-02-03 22:15 | 45691.9271 | 0.024575 | 0.00015359 | 4 | 640 | Unplanned | Lightning | Replace fuse
1193 |  | 3492 | Ohuka Road | Wairoa | Ruakituri 2003 | 2025-02-04 09:06 | 45692.3792 | 2025-02-04 14:40 | 45692.6111 | 0.12825 | 0.00038398 | 10 | 1670.6412 | Planned | Planned | Replace 11kV poles
1194 |  | 3491 | 4258 Te Araroa Road | Gisborne | Te Araroa 0103 | 2025-02-04 10:01 | 45692.4174 | 2025-02-04 11:17 | 45692.4701 | 0.0087548 | 0.00011519 | 3 | 114.0311 | Planned | Planned | Upgrade TX J280
1195 |  | 3493 | Ohuka Road | Wairoa | Ruakituri 2003 | 2025-02-05 09:14 | 45693.3847 | 2025-02-05 13:56 | 45693.5806 | 0.10828 | 0.00038398 | 10 | 1410.6336 | Planned | Planned | Replace 11kV poles & TX
1196 |  | 144940 | 143 Matanui Road | Gisborne | Tauwhareparae 0404 | 2025-02-05 10:49 | 45693.4507 | 2025-02-05 12:50 | 45693.5347 | 0.0092923 | 7.6796e-05 | 2 | 242 | Unplanned | Unknown cause | Replace fuse
1197 |  | 30052 | Browns Beach Road | Gisborne | Muriwai 0905 | 2025-02-07 14:28 | 45695.6028 | 2025-02-08 08:56 | 45696.3722 | 0.092155 | 0.00023039 | 6 | 2400 | Unplanned | Defective Equipment | Replace faulty TX
1198 |  | 30749 | Tauwharepaere | Gisborne | Tauwhareparae 0404 | 2025-02-08 11:34 | 45696.4819 | 2025-02-10 16:37 | 45698.6924 | 0.40671 | 0.0020351 | 53 | 10592 | Unplanned | Third Party Interference | Replace Poles & conductor after tree-feller brought tree down through line
1199 |  | 30053 | Morere | Wairoa | Morere 3401 | 2025-02-08 19:06 | 45696.7958 | 2025-02-09 15:24 | 45697.6417 | 0.68921 | 0.0032638 | 85 | 17949 | Unplanned | Adverse Environment | Large slip, slow moving causes wire to tension up and snap
1200 |  | 30054 | Back Ormond Road / Waimata Valley | Gisborne | Waimata 0903 | 2025-02-08 22:01 | 45696.9174 | 2025-02-09 15:18 | 45697.6375 | 1.5124 | 0.027339 | 712 | 39388 | Unplanned | Third Party Interference | Car hit Pole
1201 |  | N/A 70 | Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2025-02-08 23:45 | 45696.9896 | 2025-02-08 23:54 | 45696.9958 | 0.050455 | 0.0056061 | 146 | 1314 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over
1202 |  | N/A 70 | Tolaga Bay | Gisborne | Toko Tie 0401 | 2025-02-08 23:45 | 45696.9896 | 2025-02-08 23:56 | 45696.9972 | 0.03548 | 0.0032254 | 84 | 924 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over
1203 |  | N/A 70 | Tolaga Bay | Gisborne | Town 0402 | 2025-02-08 23:45 | 45696.9896 | 2025-02-08 23:56 | 45696.9972 | 0.086588 | 0.0078716 | 205 | 2255 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over
1204 |  | N/A 70 | Tolaga Bay | Gisborne | Rototahi 0403 | 2025-02-08 23:45 | 45696.9896 | 2025-02-08 23:57 | 45696.9979 | 0.099528 | 0.008294 | 216 | 2592 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over
1205 |  | N/A 70 | Tolaga Bay | Gisborne | Tolaga Bay Sub | 2025-02-08 23:45 | 45696.9896 | 2025-02-08 23:53 | 45696.9951 | 0.00030718 | 3.8398e-05 | 1 | 8 | Unplanned | Unknown cause | Patrol no cause found. Suspect insulator flash over
1206 |  | 148093 | 279 Tahora Settlement Road | Gisborne | Tahora 1103 | 2025-02-09 18:36 | 45697.775 | 2025-02-09 21:20 | 45697.8889 | 0.15113 | 0.00092155 | 24 | 3936 | Unplanned | Unknown cause | Replace fuse
1207 |  | 148378 | 183 Tuparoa Road | Gisborne | Ruatoria 0201 | 2025-02-10 07:43 | 45698.3215 | 2025-02-10 09:23 | 45698.391 | 0.076796 | 0.00076796 | 20 | 2000 | Unplanned | Wildlife | Replace fuses
1208 |  | 3515 | Lake, Village, Ruakituri | Wairoa | Tuai Sub | 2025-02-11 06:45 | 45699.2812 | 2025-02-11 17:33 | 45699.7312 | 0.026955 | 0.026955 | 702 | 702 | Planned | Planned | Transpower disconnector maintenance @ Tuai
1209 |  | N/A 71 | Tolaga Bay Sub | Gisborne | Rototahi 0403 | 2025-02-11 07:39 | 45699.3187 | 2025-02-11 07:48 | 45699.325 | 0.074646 | 0.008294 | 216 | 1944 | Unplanned | Human Error | Open 50kV CB H14 as part of SW3498. H14 was suppling Tolaga Bay as the Gis - Tol 50kV was under fault conditions
1210 |  | N/A 71 | Tolaga Bay Sub | Gisborne | Town 0402 | 2025-02-11 07:39 | 45699.3187 | 2025-02-11 07:50 | 45699.3264 | 0.086588 | 0.0078716 | 205 | 2255 | Unplanned | Human Error | Open 50kV CB H14 as part of SW3498. H14 was suppling Tolaga Bay as the Gis - Tol 50kV was under fault conditions
1211 |  | N/A 71 | Tolaga Bay Sub | Gisborne | Toko Tie 0401 | 2025-02-11 07:39 | 45699.3187 | 2025-02-11 07:50 | 45699.3264 | 0.03548 | 0.0032254 | 84 | 924 | Unplanned | Human Error | Open 50kV CB H14 as part of SW3498. H14 was suppling Tolaga Bay as the Gis - Tol 50kV was under fault conditions
1212 |  | N/A 71 | Tolaga Bay Sub | Gisborne | Tauwhareparae 0404 | 2025-02-11 07:39 | 45699.3187 | 2025-02-11 07:50 | 45699.3264 | 0.061667 | 0.0056061 | 146 | 1606 | Unplanned | Human Error | Open 50kV CB H14 as part of SW3498. H14 was suppling Tolaga Bay as the Gis - Tol 50kV was under fault conditions
1213 |  | 3498 | Waiapu Road | Gisborne | Inland 0301 | 2025-02-11 07:56 | 45699.3306 | 2025-02-11 14:32 | 45699.6056 | 0.36079 | 0.0017279 | 45 | 5164.3129 | Unplanned | Human Error | Switching error
1214 |  | 30005 | Peel Street | Gisborne | Reads Quay 0603 | 2025-02-11 08:24 | 45699.35 | 2025-02-11 20:05 | 45699.8368 | 0.013171 | 0.00030718 | 8 | 343 | Unplanned | Defective Equipment | Replace faulty TX
1215 |  | 3498 A | Waiapu Road | Gisborne | Inland 0301 | 2025-02-11 15:22 | 45699.6403 | 2025-02-11 15:25 | 45699.6424 | 0.15321 | 0.051069 | 1330 | 0 | Planned | Planned | Replace 50kV poles
1216 |  | 30010 | Matawai Rd, Bushmere Road | Gisborne | Waimata 0903 | 2025-02-11 22:11 | 45699.9243 | 2025-02-11 22:51 | 45699.9521 | 0.11827 | 0.0029566 | 77 | 3080 | Unplanned | Defective Equipment | Blown jumper on Links D4318
1217 |  | 3495 | Waireka Road | Wairoa | Frasertown 3103 | 2025-02-12 09:03 | 45700.3771 | 2025-02-12 13:05 | 45700.5451 | 0.13009 | 0.00053757 | 14 | 3388 | Planned | Planned | Replace pole W5019
1218 |  | 149956 | 195 Russell Road, Ngatapa | Gisborne | Ngatapa 1102 | 2025-02-12 17:40 | 45700.7361 | 2025-02-12 19:00 | 45700.7917 | 0.03379 | 0.00042238 | 11 | 880 | Unplanned | Unknown cause | Replace fuse
1219 |  | 30015 | Tiniroto Rd / Lavenham Rd | Gisborne | Lavenham 0902 | 2025-02-13 13:43 | 45701.5715 | 2025-02-13 16:31 | 45701.6882 | 0.62504 | 0.017241 | 449 | 16278 | Unplanned | Third Party Interference | Pole D1389 down due to Car V's Pole D1389
1220 |  | 3501 | Tokomaru Bay | Gisborne | Rua-Te Araroa 50kV | 2025-02-13 14:29 | 45701.6035 | 2025-02-13 14:30 | 45701.6042 | 0.018201 | 0.018201 | 474 | 0 | Planned | Planned | Replacing 50kV Poles
1221 |  | 1710 A | Tauwhareparae Rd | Gisborne | Tauwhareparae 0404 | 2025-02-14 09:02 | 45702.3764 | 2025-02-14 12:42 | 45702.5292 | 0.41731 | 0.0020351 | 53 | 10868 | Planned | Planned | Replace poles & conductor after tree-feller brought tree down through line
1222 |  | 151086 | 207 Rockhill Road | Gisborne | W O Kuri 1001 | 2025-02-14 10:17 | 45702.4285 | 2025-02-14 12:20 | 45702.5139 | 0.014169 | 0.00011519 | 3 | 369 | Unplanned | Unknown cause | Replace fuse
1223 |  | 150887 | 1926 Rakaroa Road | Gisborne | Matawai 1204 | 2025-02-14 20:44 | 45702.8639 | 2025-02-15 00:10 | 45703.0069 | 0.08701 | 0.00042238 | 11 | 2266 | Unplanned | Lightning | Replace fuse
1224 |  | 152519 | 109 Shanks Road | Gisborne | Te Arai 0906 | 2025-02-16 07:29 | 45704.3118 | 2025-02-16 09:30 | 45704.3958 | 0.023231 | 0.00019199 | 5 | 605 | Unplanned | Unknown cause | Replace fuses
1225 |  | 3509 | Gladstone Rd / Lytton Rd | Gisborne | Lytton 0701 | 2025-02-16 08:31 | 45704.3549 | 2025-02-16 12:30 | 45704.5208 | 0.68828 | 0.0028799 | 75 | 8994.8983 | Planned | Planned | Replace TX B94
1226 |  | 30058 | Ruakaka Road | Gisborne | Tiniroto 1003 | 2025-02-16 08:49 | 45704.3674 | 2025-02-16 09:56 | 45704.4139 | 0.036017 | 0.00053757 | 14 | 938 | Unplanned | Defective Equipment | Cracked insulator @ HV fuses D295
1227 |  | 153233 | 673 Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2025-02-17 08:33 | 45705.3562 | 2025-02-17 10:00 | 45705.4167 | 0.013363 | 0.00015359 | 4 | 348 | Unplanned | Unknown cause | Replace fuses
1228 |  | 30022 | Waima | Gisborne | Seaside 0302 | 2025-02-17 10:16 | 45705.4278 | 2025-02-17 11:06 | 45705.4625 | 0.092155 | 0.0018431 | 48 | 2400 | Unplanned | Vegetation | Tree through 11kV lind at pole H2679
1229 |  | 30024 | waima | Gisborne | Seaside 0302 | 2025-02-17 14:04 | 45705.5861 | 2025-02-17 17:05 | 45705.7118 | 0.3336 | 0.0018431 | 48 | 8688 | Unplanned | Vegetation | Tree brought down through 11kV
1230 |  | 3503 | Wheatstone Road | Gisborne | Dalton 0502 | 2025-02-18 08:32 | 45706.3556 | 2025-02-18 12:34 | 45706.5236 | 0.26948 | 0.0011135 | 29 | 3514.8127 | Planned | Planned | 3503/1 Max McLean installed HV Pole & TX A292. 3503 Electrinet unable to complete work due to wind conditions
1231 |  | 3494 | Putere Road | Wairoa | Raupunga 3101 | 2025-02-18 09:03 | 45706.3771 | 2025-02-18 13:29 | 45706.5618 | 0.24513 | 0.00092155 | 24 | 3195.3176 | Planned | Planned | Replace pole W5096
1232 |  | 153888 | 21 Makatote Rd, Waipiro | Gisborne | Makarika 0204 | 2025-02-18 09:06 | 45706.3792 | 2025-02-18 12:24 | 45706.5167 | 0.11404 | 0.00057597 | 15 | 2970 | Unplanned | Defective Equipment | Replace fuses
1233 |  | 30028 | Puhinga Road | Gisborne | Makarika 0204 | 2025-02-18 11:54 | 45706.4958 | 2025-02-18 12:24 | 45706.5167 | 0.017279 | 0.00057597 | 15 | 450 | Unplanned | Defective Equipment | Resag conductor @ pole H1575
1234 |  | 154511 | 31 Tiniroto Road, | Wairoa | Frasertown 3103 | 2025-02-19 06:12 | 45707.2583 | 2025-02-19 07:40 | 45707.3194 | 0.0067581 | 7.6796e-05 | 2 | 176 | Unplanned | Unknown cause | Replace fuses
1235 |  | 154537 | Beach Road, Tokomaru Bay | Gisborne | Seaside 0302 | 2025-02-19 07:10 | 45707.2986 | 2025-02-19 09:45 | 45707.4062 | 0.28568 | 0.0018431 | 48 | 7440 | Unplanned | Wildlife | Replace fuses
1236 |  | 30069 | Wainui Rd / Wheatstone Road | Gisborne | Tamarau 0503 | 2025-02-19 08:32 | 45707.3556 | 2025-02-19 14:12 | 45707.5917 | 1.1666 | 0.040587 | 1057 | 30382 | Unplanned | Third Party Interference | Digger came in contact with the OH lind @ Pole A4287 & LV line touched HV. Broken LV X-Arm, LV line down and TX A59 failed (faulty)
1237 |  | 3512 | Jacob Lane | Gisborne | Nelson 0803 | 2025-02-19 08:39 | 45707.3604 | 2025-02-19 16:18 | 45707.6792 | 0.12337 | 0.00026879 | 7 | 1606.9318 | Planned | Planned | Replace TX C646
1238 |  | 3514 | Pa Road | Gisborne | Dalton 0502 | 2025-02-19 09:08 | 45707.3806 | 2025-02-19 13:04 | 45707.5444 | 0.16311 | 0.00069116 | 18 | 2125.8661 | Planned | Planned | Replace/Relocate 400V pole mtce TX A123
1239 |  | 30035 | 92 Lavenham Road | Gisborne | Lavenham 0902 | 2025-02-20 08:24 | 45708.35 | 2025-02-20 11:17 | 45708.4701 | 0.039857 | 0.00023039 | 6 | 1038 | Unplanned | Third Party Interference | Car V's Pole - @ Pole D2011
1240 |  | 3511 | Waikura Road | Gisborne | Hicks Bay 0102 | 2025-02-20 08:33 | 45708.3562 | 2025-02-20 13:28 | 45708.5611 | 0.44177 | 0.0014975 | 39 | 5762.1366 | Planned | Planned | Replace pole J4219
1241 |  | 30074 | Waitahaia Rd / Mata Rd | Gisborne | Mata 0304 | 2025-02-20 08:47 | 45708.366 | 2025-02-20 12:43 | 45708.5299 | 0.18923 | 0.00080636 | 21 | 4928 | Unplanned | Defective Equipment | Broken insulator at pole H4496
1242 |  | 3502 A | Lake Road | Wairoa | Frasertown 3103 | 2025-02-20 09:00 | 45708.375 | 2025-02-20 09:03 | 45708.3771 | 0.0018431 | 0.00061437 | 16 | 24.0147 | Planned | Planned | Replace ABS W982
1243 |  | 3502 | Lake Road | Wairoa | Frasertown 3103 | 2025-02-20 09:00 | 45708.375 | 2025-02-20 14:35 | 45708.6076 | 1.3362 | 0.0040702 | 106 | 17431.936 | Planned | Planned | Replace ABS W982
1244 |  | 155298 | 497 Ormond Valley Road | Gisborne | Waimata 0903 | 2025-02-20 11:13 | 45708.4674 | 2025-02-20 13:40 | 45708.5694 | 0.19191 | 0.0013055 | 34 | 4998 | Unplanned | Unknown cause | Replace fuse
1245 |  | 155433 | 298 Ormond Valley Road | Gisborne | Waimata 0903 | 2025-02-20 14:43 | 45708.6132 | 2025-02-20 15:40 | 45708.6528 | 0.0021887 | 3.8398e-05 | 1 | 57 | Unplanned | Unknown cause | Replace fus
1246 |  | 3510 A | Waikura Valley Road | Gisborne | Hicks Bay 0102 | 2025-02-21 08:33 | 45709.3562 | 2025-02-21 12:32 | 45709.5222 | 0.35791 | 0.0014975 | 39 | 9321 | Planned | Planned | Replace poles
1247 |  | 156158 | 2317 Kanakania Road | Gisborne | Kanakanaia 1202 | 2025-02-21 16:22 | 45709.6819 | 2025-02-21 19:30 | 45709.8125 | 0.0072188 | 3.8398e-05 | 1 | 188 | Unplanned | Vegetation | Replace fuses
1248 |  | 30078 | Mahia Penensular | Wairoa | Mahia 3301 | 2025-02-22 01:58 | 45710.0819 | 2025-02-22 11:35 | 45710.4826 | 3.5951 | 0.016242 | 423 | 93627 | Unplanned | Defective Equipment | Cracked glass insulator burnt arm, pulled through
1249 |  | 3513 | Taumata Road | Gisborne | Tahora 1103 | 2025-02-22 08:33 | 45710.3562 | 2025-02-22 14:35 | 45710.6076 | 0.097301 | 0.00026879 | 7 | 1267.3669 | Planned | Planned | Replace poles
1250 |  | 157604 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-02-23 11:39 | 45711.4854 | 2025-02-23 13:00 | 45711.5417 | 0.018661 | 0.00023039 | 6 | 486 | Unplanned | Unknown cause | Replace fuses
1251 |  | 3518 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-02-24 09:04 | 45712.3778 | 2025-02-24 14:59 | 45712.6243 | 0.2181 | 0.00061437 | 16 | 2841.7448 | Planned | Planned | Cut trees
1252 |  | 3516 | Waihi Road | Wairoa | Frasertown 3103 | 2025-02-25 09:03 | 45713.3771 | 2025-02-25 14:44 | 45713.6139 | 0.14403 | 0.00042238 | 11 | 1876.2922 | Planned | Planned | Replace 11kV pole
1253 |  | 3523 | Te Araroa | Gisborne | Awatere 0101 | 2025-02-25 09:04 | 45713.3778 | 2025-02-25 13:24 | 45713.5583 | 0.099835 | 0.00038398 | 10 | 1300.6336 | Planned | Planned | Change 50kV poles
1254 |  | N/A 75 | Wharerata Road | Gisborne | Muriwai 0905 | 2025-02-25 10:10 | 45713.4236 | 2025-02-25 11:06 | 45713.4625 | 0.25343 | 0.0051453 | 134 | 6600 | Unplanned | Human Error | Cut tree branch, contacted HV conductor
1255 |  | N/A 72 | Tolaga Sub | Gisborne | Rototahi 0403 | 2025-02-25 12:29 | 45713.5201 | 2025-02-25 12:39 | 45713.5271 | 0.061821 | 0.0061821 | 161 | 1610 | Unplanned | Wildlife | Flock of Canadian goose birds located in the area
1256 |  | N/A 72 | Tolaga Sub | Gisborne | Town 0402 | 2025-02-25 12:29 | 45713.5201 | 2025-02-25 12:45 | 45713.5312 | 0.12595 | 0.0078716 | 205 | 3280 | Unplanned | Wildlife | Flock of Canadian goose birds located in the area
1257 |  | N/A 72 | Tolaga Sub | Gisborne | Toko Tie 0401 | 2025-02-25 12:29 | 45713.5201 | 2025-02-25 12:47 | 45713.5326 | 0.058058 | 0.0032254 | 84 | 1512 | Unplanned | Wildlife | Flock of Canadian goose birds located in the area
1258 |  | N/A 72 | Tolaga Sub | Gisborne | Tauwhareparae 0404 | 2025-02-25 12:29 | 45713.5201 | 2025-02-25 12:47 | 45713.5326 | 0.10091 | 0.0056061 | 146 | 2628 | Unplanned | Wildlife | Flock of Canadian goose birds located in the area
1259 |  | 158959 | 75 Maraehara Road | Gisborne | Tiki Tiki 0206 | 2025-02-25 14:31 | 45713.6049 | 2025-02-25 17:00 | 45713.7083 | 0.0057213 | 3.8398e-05 | 1 | 149 | Unplanned | Wildlife | Replace fuses
1260 |  | 159055 | 171 Pauakiri Road | Gisborne | Mata 0304 | 2025-02-25 17:18 | 45713.7208 | 2025-02-25 18:40 | 45713.7778 | 0.012595 | 0.00015359 | 4 | 328 | Unplanned | Wildlife | Replace fuses
1261 |  | 159702 | 1584 Mangapoike Road | Wairoa | Frasertown 3103 | 2025-02-26 17:29 | 45714.7285 | 2025-02-26 19:00 | 45714.7917 | 0.0069884 | 7.6796e-05 | 2 | 182 | Unplanned | Unknown cause | Replace fuse
1262 |  | 159673 | 48 Mangamaia Road | Gisborne | Whatatutu 1201 | 2025-02-26 17:29 | 45714.7285 | 2025-02-26 19:45 | 45714.8229 | 0.13055 | 0.00095995 | 25 | 3400 | Unplanned | Unknown cause | Replace fuse
1263 |  | 160078 | 187 Berry Road | Gisborne | Tiniroto 1003 | 2025-02-27 08:33 | 45715.3562 | 2025-02-27 11:30 | 45715.4792 | 0.09515 | 0.00053757 | 14 | 2478 | Unplanned | Unknown cause | Replace fuses
1264 |  | 3522 | Lake Road | Wairoa | Frasertown 3103 | 2025-02-27 09:02 | 45715.3764 | 2025-02-27 17:01 | 45715.709 | 1.8393 | 0.0038398 | 100 | 20980.2519 | Planned | Planned | Replace poles
1265 |  | 30045 | Mangamaia Road | Gisborne | Whatatutu 1201 | 2025-02-27 11:24 | 45715.475 | 2025-02-27 12:08 | 45715.5056 | 0.042238 | 0.00095995 | 25 | 1100 | Unplanned | Defective Equipment | Replaced insulator @ pole E2162
1266 |  | 3524 | Stanley Road | Gisborne | Lytton 0701 | 2025-02-27 17:30 | 45715.7292 | 2025-02-27 22:02 | 45715.9181 | 0.38644 | 0.0014207 | 37 | 5040.6735 | Planned | Planned | Replace GM TX
1267 |  | 3521 A | Tauwhareparae Rd | Gisborne | Rototahi 0403 | 2025-02-28 08:30 | 45716.3542 | 2025-02-28 17:01 | 45716.709 | 2.4919 | 0.0048766 | 127 | 30628.6373 | Planned | Planned | Isolate to remove roof
1268 |  | 3526 | Riverside / Goodwin Rd | Gisborne | Whangara 0506 | 2025-02-28 08:31 | 45716.3549 | 2025-02-28 16:30 | 45716.6875 | 0.9932 | 0.0020735 | 54 | 12959.8165 | Planned | Planned | Replace HV pole and install prop pole
1269 |  | 3525 A | Te Araroa Road | Gisborne | Awatere 0101 | 2025-02-28 09:04 | 45716.3778 | 2025-02-28 14:55 | 45716.6215 | 0.053911 | 0.00015359 | 4 | 702.1078 | Planned | Planned | Replace 50kV poles
1270 |  | 30049 | Managapa / Balance Village / Whataupoko | Gisborne | Aberdeen 0609 | 2025-02-28 09:49 | 45716.409 | 2025-02-28 10:29 | 45716.4368 | 1.531 | 0.096417 | 2511 | 39872 | Unplanned | Defective Equipment | HV cable failed btwn RMU B6212 - RMU B344 & switching error
1271 |  | 3525 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-02-28 16:31 | 45716.6882 | 2025-02-28 16:32 | 45716.6889 | 0.018162 | 0.018162 | 473 | 240.7954 | Planned | Planned | Replace 50kV poles
1272 |  | 3517 | Waiapu Road | Gisborne | Makarika 0204 | 2025-03-01 09:00 | 45717.375 | 2025-03-01 12:19 | 45717.5132 | 0.51131 | 0.0026111 | 68 | 6666.7145 | Planned | Planned | Cut Trees
1273 |  | 3528 | Wainui Road | Gisborne | Dalton 0502 | 2025-03-03 09:13 | 45719.384 | 2025-03-03 11:44 | 45719.4889 | 0.39427 | 0.0026111 | 68 | 5147.4052 | Planned | Planned | Cut-out sample lengths of O/Head conductor for assessment. Change cross arm @ pole A2114
1274 |  | 162864 | Browns Beach Road | Gisborne | Muriwai 0905 | 2025-03-03 11:56 | 45719.4972 | 2025-03-03 14:56 | 45719.6222 | 0.013823 | 7.6796e-05 | 2 | 360 | Unplanned | Unknown cause | Replace fuses
1275 |  | 3529 | SH35 Okitu & Makarori | Gisborne | Dalton 0502 | 2025-03-03 13:32 | 45719.5639 | 2025-03-03 15:32 | 45719.6472 | 0.31333 | 0.0026111 | 68 | 4090.6532 | Planned | Planned | Cut & replace small section of HV conductor for testing
1276 |  | 3527 | Totangi Road | Gisborne | Totangi 1101 | 2025-03-04 08:02 | 45720.3347 | 2025-03-04 16:46 | 45720.6986 | 0.41174 | 0.00080636 | 21 | 5337.411 | Planned | Planned | Tree cutting
1277 |  | 30093 | Armstrong Road | Gisborne | Whatatutu 1201 | 2025-03-05 07:57 | 45721.3313 | 2025-03-05 12:32 | 45721.5222 | 0.13117 | 0.00092155 | 24 | 3416 | Unplanned | Defective Equipment | Replace broken staywire @ pole E3507
1278 |  | 3531 | Ormond Valley Road | Gisborne | Waimata 0903 | 2025-03-05 09:36 | 45721.4 | 2025-03-05 10:49 | 45721.4507 | 0.092501 | 0.0012671 | 33 | 892.129 | Planned | Planned | Replace HV stub pole
1279 |  | N/A 74 | Tawhara Valley | Wairoa | Brickworks 3201 | 2025-03-05 12:44 | 45721.5306 | 2025-03-05 16:31 | 45721.6882 | 0.36877 | 0.0062205 | 162 | 9604 | Unplanned | Adverse Weather | Line clashing between W1138 & W1021
1280 |  | N/A 73 | Tawhara Road | Wairoa | Brickworks 3201 | 2025-03-05 18:30 | 45721.7708 | 2025-03-05 19:04 | 45721.7944 | 0.19502 | 0.0062205 | 162 | 5079 | Unplanned | Adverse Weather | Line clash between W1138 & W1021
1281 |  | 164342 | 39 Kiwi Road, Wairoa | Wairoa | Nuhaka 3203 | 2025-03-05 18:55 | 45721.7882 | 2025-03-05 21:05 | 45721.8785 | 0.014975 | 0.00011519 | 3 | 390 | Unplanned | Defective Equipment | Faulty lightning arestors
1282 |  | 30107 | Tiniroto / Ruakaka Road | Gisborne | Tiniroto 1003 | 2025-03-05 23:18 | 45721.9708 | 2025-03-06 16:16 | 45722.6778 | 0.79046 | 0.0031486 | 82 | 20586 | Unplanned | Vegetation | 3 span HV down Poles D3536 - D310. Tree thru line
1283 |  | 30106 | Panikau Road | Gisborne | Dalton 0502 | 2025-03-06 04:23 | 45722.1826 | 2025-03-06 14:15 | 45722.5938 | 0.66713 | 0.0021503 | 56 | 17374 | Unplanned | Vegetation | Tree branch through HV lines byd HV fuses A168 at pole A3779
1284 |  | 30152 | Waihua Valley Rd / Cricklewood Rd | Wairoa | Raupunga 3101 | 2025-03-06 11:03 | 45722.4604 | 2025-03-06 16:19 | 45722.6799 | 0.26694 | 0.00084476 | 22 | 6952 | Unplanned | Adverse Weather | Repair conductor after clash, high winds
1285 |  | 30109 | Wairoa / Mahia Region | Wairoa | Mahia 3301 | 2025-03-06 13:04 | 45722.5444 | 2025-03-07 18:24 | 45723.7667 | 2.9773 | 0.11132 | 2899 | 77538 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1286 |  | 30109 | Wairoa / Mahia Region | Wairoa | Morere 3401 | 2025-03-06 13:04 | 45722.5444 | 2025-03-07 18:22 | 45723.7653 | 0.66598 | 0.020581 | 536 | 17344 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1287 |  | 165300 | 2753 Whangara Road | Gisborne | Rototahi 0403 | 2025-03-07 09:28 | 45723.3944 | 2025-03-07 11:02 | 45723.4597 | 0.0036094 | 3.8398e-05 | 1 | 94 | Unplanned | Adverse Weather | Replace fuses
1288 |  | 30109 | Wairoa / Mahia Region | Wairoa | Frasertown 3103 | 2025-03-07 17:59 | 45723.7493 | 2025-03-07 18:02 | 45723.7514 | 0.055408 | 0.018469 | 481 | 1443 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1289 |  | 30109 | Wairoa / Mahia Region | Wairoa | Brickworks 3201 | 2025-03-07 17:59 | 45723.7493 | 2025-03-07 18:02 | 45723.7514 | 0.07096 | 0.023653 | 616 | 1848 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1290 |  | 30109 | Wairoa / Mahia Region | Wairoa | Borough Two 3205 | 2025-03-07 17:59 | 45723.7493 | 2025-03-07 18:02 | 45723.7514 | 0.076374 | 0.025458 | 663 | 1989 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1291 |  | 30109 | Wairoa / Mahia Region | Wairoa | Borough One 3204 | 2025-03-07 17:59 | 45723.7493 | 2025-03-07 18:02 | 45723.7514 | 0.094344 | 0.031448 | 819 | 2457 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1292 |  | 30109 | Wairoa / Mahia Region | Wairoa | Affco 3202 | 2025-03-07 17:59 | 45723.7493 | 2025-03-07 18:22 | 45723.7653 | 0.032677 | 0.0014207 | 37 | 851 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1293 |  | 30109 | Wairoa / Mahia Region | Wairoa | Nuhaka 3203 | 2025-03-07 17:59 | 45723.7493 | 2025-03-07 18:21 | 45723.7646 | 0.16726 | 0.0076028 | 198 | 4356 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1294 |  | 30109 | Wairoa / Mahia Region | Wairoa | Kiwi Sub 32 | 2025-03-07 17:59 | 45723.7493 | 2025-03-07 18:27 | 45723.7688 | 0.0010751 | 3.8398e-05 | 1 | 28 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1295 |  | 30109 | Wairoa / Mahia Region | Wairoa | Raupunga 3101 | 2025-03-07 17:59 | 45723.7493 | 2025-03-07 18:11 | 45723.7576 | 0.19399 | 0.016166 | 421 | 5052 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1296 |  | 30109 | Wairoa / Mahia Region | Wairoa | Wairoa Sub 31 | 2025-03-07 17:59 | 45723.7493 | 2025-03-07 18:02 | 45723.7514 | 0.00023039 | 7.6796e-05 | 2 | 6 | Unplanned | Defective Equipment | Faulty Insulator Failed - Conductor on Arm Burnt Down Pole
1297 |  | 165674 | Whakaki | Wairoa | Nuhaka 3203 | 2025-03-07 19:15 | 45723.8021 | 2025-03-08 11:45 | 45724.4896 | 1.9387 | 0.0019583 | 51 | 50490 | Unplanned | Unknown cause | Replace fuses
1298 |  | 30110 | Moana Road | Gisborne | Dalton 0502 | 2025-03-08 05:59 | 45724.2493 | 2025-03-08 08:48 | 45724.3667 | 0.89552 | 0.0052989 | 138 | 23322 | Unplanned | Adverse Weather | ABS A2188 arcing across shackles - Salt Build Up
1299 |  | 3554 | Nelson Road | Gisborne | Nelson 0803 | 2025-03-08 09:00 | 45724.375 | 2025-03-08 17:41 | 45724.7368 | 0.020005 | 3.8398e-05 | 1 | 521 | Planned | Planned | Upgrade 400V fuse rack TX C325
1300 |  | N/A 76 | SH2 Whakaki | Wairoa | Nuhaka 3203 | 2025-03-08 11:39 | 45724.4854 | 2025-03-08 11:45 | 45724.4896 | 0.0025343 | 0.00042238 | 11 | 66 | Unplanned | Defective Equipment | Blown 40a fuse - centre phase @ W8167
1301 |  | 166888 | 180Monck Road | Gisborne | Waimata 0903 | 2025-03-09 09:45 | 45725.4062 | 2025-03-09 11:00 | 45725.4583 | 0.0028799 | 3.8398e-05 | 1 | 75 | Unplanned | Lightning | Replace fuse
1302 |  | 30113 | Waimata Valley Road | Gisborne | Waimata 0903 | 2025-03-09 10:09 | 45725.4229 | 2025-03-10 10:12 | 45726.425 | 0.11082 | 7.6796e-05 | 2 | 2886 | Unplanned | Lightning | Faulty Transformer G188 caused by Lightning in the area
1303 |  | 3550 | Waimoatatini | Gisborne | Tiki Tiki 0206 | 2025-03-10 09:00 | 45726.375 | 2025-03-10 12:36 | 45726.525 | 0.21564 | 0.00099835 | 26 | 5616 | Planned | Planned | Replace Switch J1048
1304 |  | 3534 | Lucknow Street | Wairoa | Borough Two 3205 | 2025-03-10 09:32 | 45726.3972 | 2025-03-10 10:35 | 45726.441 | 0.24433 | 0.0038782 | 101 | 3216.7529 | Planned | Planned | Replace X-arm
1305 |  | 167733 | 1400 Wharerata Road | Gisborne | Muriwai 0905 | 2025-03-10 12:26 | 45726.5181 | 2025-03-10 13:45 | 45726.5729 | 0.0030334 | 3.8398e-05 | 1 | 79 | Unplanned | Vegetation | Tree in lines
1306 |  | N/A 77 | Whakaangiangi Road | Gisborne | Awatere 0101 | 2025-03-11 01:15 | 45727.0521 | 2025-03-11 08:29 | 45727.3535 | 0.51503 | 0.0012287 | 32 | 13413 | Unplanned | Wildlife | Possum on Pole J2997 - Centre phase
1307 |  | 3563 | Renner Road | Gisborne | Lavenham 0902 | 2025-03-11 08:51 | 45727.3688 | 2025-03-12 16:48 | 45728.7 | 1.1777 | 0.00061437 | 16 | 30672 | Planned | Planned | Problem with pole, left off overnight, fixed next day
1308 |  | 3536 | Mahia | Wairoa | Mahia 3301 | 2025-03-11 09:00 | 45727.375 | 2025-03-11 11:11 | 45727.466 | 1.8762 | 0.014322 | 373 | 48863 | Unplanned | Human Error | Shutdown cancelled as customer notification failed due to alternative date 12/2/25
1309 |  | 168534 | 202 Otoi Road | Wairoa | Raupunga 3101 | 2025-03-11 16:40 | 45727.6944 | 2025-03-11 18:00 | 45727.75 | 0.0030718 | 3.8398e-05 | 1 | 80 | Unplanned | Unknown cause | Replace fuse
1310 |  | N/A 78 | 50kV Ring | Gisborne | Patutahi Sub 09 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.0014975 | 3.8398e-05 | 1 | 39 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1311 |  | N/A 78 | 50kV Ring | Gisborne | Lavenham 0902 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.67239 | 0.017241 | 449 | 17511 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1312 |  | N/A 78 | 50kV Ring | Gisborne | Waimata 0903 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.97189 | 0.02492 | 649 | 25311 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1313 |  | N/A 78 | 50kV Ring | Gisborne | Muriwai 0905 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.61848 | 0.015858 | 413 | 16107 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1314 |  | N/A 78 | 50kV Ring | Gisborne | Te Arai 0906 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.35042 | 0.0089851 | 234 | 9126 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1315 |  | N/A 78 | 50kV Ring | Gisborne | Pehiri Sub 10 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.0014975 | 3.8398e-05 | 1 | 39 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1316 |  | N/A 78 | 50kV Ring | Gisborne | W O Kuri 1001 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.070384 | 0.0018047 | 47 | 1833 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1317 |  | N/A 78 | 50kV Ring | Gisborne | Parikanapa 1002 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.044926 | 0.0011519 | 30 | 1170 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1318 |  | N/A 78 | 50kV Ring | Gisborne | Tiniroto 1003 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.18719 | 0.0047998 | 125 | 4875 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1319 |  | N/A 78 | 50kV Ring | Gisborne | Tahunga 1004 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.073379 | 0.0018815 | 49 | 1911 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1320 |  | N/A 78 | 50kV Ring | Gisborne | Ngatapa Sub 11 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.0014975 | 3.8398e-05 | 1 | 39 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1321 |  | N/A 78 | 50kV Ring | Gisborne | Totangi 1101 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.020965 | 0.00053757 | 14 | 546 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1322 |  | N/A 78 | 50kV Ring | Gisborne | Ngatapa 1102 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.10483 | 0.0026879 | 70 | 2730 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1323 |  | N/A 78 | 50kV Ring | Gisborne | Tahora 1103 | 2025-03-11 23:17 | 45727.9701 | 2025-03-11 23:56 | 45727.9972 | 0.22613 | 0.0057981 | 151 | 5889 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1324 |  | N/A 78 | 50kV Ring | Gisborne | Puha Sub 12 | 2025-03-11 23:17 | 45727.9701 | 2025-03-12 00:02 | 45728.0014 | 0.0017279 | 3.8398e-05 | 1 | 45 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1325 |  | N/A 78 | 50kV Ring | Gisborne | Whatatutu 1201 | 2025-03-11 23:17 | 45727.9701 | 2025-03-12 00:02 | 45728.0014 | 0.42161 | 0.0093691 | 244 | 10980 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1326 |  | N/A 78 | 50kV Ring | Gisborne | Kanakanaia 1202 | 2025-03-11 23:17 | 45727.9701 | 2025-03-12 00:02 | 45728.0014 | 0.3093 | 0.0068732 | 179 | 8055 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1327 |  | N/A 78 | 50kV Ring | Gisborne | Te Karaka 1203 | 2025-03-11 23:17 | 45727.9701 | 2025-03-12 00:02 | 45728.0014 | 0.31448 | 0.0069884 | 182 | 8190 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1328 |  | N/A 78 | 50kV Ring | Gisborne | Matawai 1204 | 2025-03-11 23:17 | 45727.9701 | 2025-03-12 00:02 | 45728.0014 | 0.66525 | 0.014783 | 385 | 17325 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1329 |  | N/A 78 | 50kV Ring | Gisborne | Dunstan 1403 | 2025-03-11 23:17 | 45727.9701 | 2025-03-12 | 45728 | 0.018162 | 0.00042238 | 11 | 473 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1330 |  | N/A 78 | 50kV Ring | Gisborne | JNL_A 1405 | 2025-03-11 23:17 | 45727.9701 | 2025-03-12 | 45728 | 0.033022 | 0.00076796 | 20 | 860 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1331 |  | N/A 78 | 50kV Ring | Gisborne | Bell 1406 | 2025-03-11 23:17 | 45727.9701 | 2025-03-12 | 45728 | 0.39131 | 0.0091003 | 237 | 10191 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1332 |  | N/A 78 | 50kV Ring | Gisborne | Waipaoa 1408 | 2025-03-11 23:17 | 45727.9701 | 2025-03-12 | 45728 | 0.0099067 | 0.00023039 | 6 | 258 | Unplanned | Unknown cause | Patrol line and could not locate any fault. 2nd Foot Patrol Done - Nothing Found
1333 |  | 3506 A | Tokomaru Bay Sub | Gisborne | Ruatoria Sub 02 | 2025-03-12 16:17 | 45728.6785 | 2025-03-12 16:18 | 45728.6792 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | 50Kv S/Gear maintenance
1334 |  | 3506 A | Tokomaru Bay Sub | Gisborne | Ruatoria 0201 | 2025-03-12 16:17 | 45728.6785 | 2025-03-12 16:18 | 45728.6792 | 0.011903 | 0.011903 | 310 | 156.845 | Planned | Planned | 50Kv S/Gear maintenance
1335 |  | 3506 A | Tokomaru Bay Sub | Gisborne | Makarika 0204 | 2025-03-12 16:17 | 45728.6785 | 2025-03-12 16:18 | 45728.6792 | 0.004339 | 0.004339 | 113 | 56.7452 | Planned | Planned | 50Kv S/Gear maintenance
1336 |  | 3506 A | Tokomaru Bay Sub | Gisborne | Tiki Tiki 0206 | 2025-03-12 16:17 | 45728.6785 | 2025-03-12 16:18 | 45728.6792 | 0.012134 | 0.012134 | 316 | 159.9171 | Planned | Planned | 50Kv S/Gear maintenance
1337 |  | 3506 A | Tokomaru Bay Sub | Gisborne | Tokomaru Bay Sub 03 | 2025-03-12 16:17 | 45728.6785 | 2025-03-12 16:18 | 45728.6792 | 7.6796e-05 | 7.6796e-05 | 2 | 1.0001 | Planned | Planned | 50Kv S/Gear maintenance
1338 |  | 3506 A | Tokomaru Bay Sub | Gisborne | Inland 0301 | 2025-03-12 16:17 | 45728.6785 | 2025-03-12 16:18 | 45728.6792 | 0.0061437 | 0.0061437 | 160 | 80.4915 | Planned | Planned | 50Kv S/Gear maintenance
1339 |  | 3506 A | Tokomaru Bay Sub | Gisborne | Seaside 0302 | 2025-03-12 16:17 | 45728.6785 | 2025-03-12 16:18 | 45728.6792 | 0.004531 | 0.004531 | 118 | 59.2673 | Planned | Planned | 50Kv S/Gear maintenance
1340 |  | 3506 | Tokomaru Bay Sub | Gisborne | Te Araroa Sub 01 | 2025-03-12 16:30 | 45728.6875 | 2025-03-12 16:31 | 45728.6882 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | 50Kv S/Gear maintenance
1341 |  | 3506 | Tokomaru Bay Sub | Gisborne | Awatere 0101 | 2025-03-12 16:30 | 45728.6875 | 2025-03-12 16:31 | 45728.6882 | 0.0033022 | 0.0033022 | 86 | 43.142 | Planned | Planned | 50Kv S/Gear maintenance
1342 |  | 3506 | Tokomaru Bay Sub | Gisborne | Hicks Bay 0102 | 2025-03-12 16:30 | 45728.6875 | 2025-03-12 16:31 | 45728.6882 | 0.0098299 | 0.0098299 | 256 | 129.2582 | Planned | Planned | 50Kv S/Gear maintenance
1343 |  | 3506 | Tokomaru Bay Sub | Gisborne | Te Araroa 0103 | 2025-03-12 16:30 | 45728.6875 | 2025-03-12 16:31 | 45728.6882 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | 50Kv S/Gear maintenance
1344 |  | 3553 | Tawhara Valley | Wairoa | Brickworks 3201 | 2025-03-13 09:01 | 45729.3757 | 2025-03-13 16:11 | 45729.6743 | 0.31371 | 0.00072956 | 19 | 8170 | Planned | Planned | Replace Poles
1345 |  | 3505 | Tokomaru Bay Sub | Gisborne | Te Araroa Sub 01 | 2025-03-13 16:30 | 45729.6875 | 2025-03-13 16:31 | 45729.6882 | 3.8398e-05 | 3.8398e-05 | 1 | 0.50002 | Planned | Planned | Stitch MTC
1346 |  | 3505 | Tokomaru Bay Sub | Gisborne | Awatere 0101 | 2025-03-13 16:30 | 45729.6875 | 2025-03-13 16:31 | 45729.6882 | 0.0034942 | 0.0034942 | 91 | 45.659 | Planned | Planned | Stitch MTC
1347 |  | 3505 | Tokomaru Bay Sub | Gisborne | Hicks Bay 0102 | 2025-03-13 16:30 | 45729.6875 | 2025-03-13 16:31 | 45729.6882 | 0.0098299 | 0.0098299 | 256 | 129.2582 | Planned | Planned | Stitch MTC
1348 |  | 3505 | Tokomaru Bay Sub | Gisborne | Te Araroa 0103 | 2025-03-13 16:30 | 45729.6875 | 2025-03-13 16:31 | 45729.6882 | 0.0049533 | 0.0049533 | 129 | 64.8195 | Planned | Planned | Stitch MTC
1349 |  | 30157 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-03-13 16:47 | 45729.6993 | 2025-03-14 14:14 | 45730.5931 | 0.015359 | 0.00030718 | 8 | 400 | Unplanned | Adverse Environment | Pole J2437A - In Slip Zone. Conductors down to 1mt above ground.
1350 |  | N/A 79 | Mahia | Wairoa | Mahia 3301 | 2025-03-15 14:15 | 45731.5938 | 2025-03-15 19:04 | 45731.7944 | 7.5869 | 0.030987 | 807 | 197586 | Unplanned | Third Party Interference | Isolate power lines for a large fire in Mahia
1351 |  | 30615 | Queen St / Paul St | Wairoa | Borough Two 3205 | 2025-03-17 13:36 | 45733.5667 | 2025-03-17 15:17 | 45733.6368 | 0.073686 | 0.00072956 | 19 | 1919 | Unplanned | Defective Equipment | 11kV cable btwn W255 - W1557 (tx) failed. Backfed through LV
1352 |  | 173027 | 1435 Waingake Road | Gisborne | Te Arai 0906 | 2025-03-18 08:54 | 45734.3708 | 2025-03-18 10:15 | 45734.4271 | 0.0031102 | 3.8398e-05 | 1 | 81 | Unplanned | Unknown cause | Replace fuse
1353 |  | 3539 | Clifton & Lyall Road | Wairoa | Frasertown 3103 | 2025-03-18 09:03 | 45734.3771 | 2025-03-18 16:15 | 45734.6771 | 0.87417 | 0.0020351 | 53 | 11399.14 | Planned | Planned | To replace 11kV poles
1354 |  | N/A 81 | Tiniroto Road | Gisborne | W O Kuri 1001 | 2025-03-19 03:01 | 45735.1257 | 2025-03-19 05:39 | 45735.2354 | 0.28272 | 0.0018047 | 47 | 7363 | Unplanned | Unknown cause | W-O-Kuri feeder tripped. Restored via Panikauapa feeder. Cause unknown. MCB Tripped on CB which prevented the spring recharge
1355 |  | N/A 80 | Waimata | Gisborne | Waimata 0903 | 2025-03-19 05:20 | 45735.2222 | 2025-03-19 07:00 | 45735.2917 | 1.1581 | 0.02492 | 649 | 30160 | Unplanned | Unknown cause | Waimata feeder tripped. Restored after sectionalisng. Cause unknown
1356 |  | 3541 | Kirkpatrick Road | Gisborne | Te Arai 0906 | 2025-03-19 10:00 | 45735.4167 | 2025-03-19 12:12 | 45735.5083 | 0.060822 | 0.00046078 | 12 | 720.3318 | Planned | Planned | Install TX fuses C2817
1357 |  | N/A 82 | Tolaga, Toko | Gisborne | Toko Tie 0401 | 2025-03-19 10:47 | 45735.4493 | 2025-03-19 11:03 | 45735.4604 | 0.11112 | 0.016703 | 435 | 2894 | Unplanned | Unknown cause | E/F thru G326 (Tokotie) tripped. Gen 5 CB 1
1358 |  | 3540 | Clifton & Lyall Road | Wairoa | Frasertown 3103 | 2025-03-20 09:00 | 45736.375 | 2025-03-20 14:49 | 45736.6174 | 0.70372 | 0.0020351 | 53 | 9176.5266 | Planned | Planned | Pole replacements - See Waihua fault
1359 |  | 3556 | Raupunga Road | Wairoa | Raupunga 3101 | 2025-03-20 09:21 | 45736.3896 | 2025-03-20 11:47 | 45736.491 | 0.022424 | 0.00015359 | 4 | 292.0922 | Planned | Planned | To connect new lines to new TX W22784
1360 |  | 30143 | Waihua | Wairoa | Raupunga 3101 | 2025-03-20 10:52 | 45736.4528 | 2025-03-21 21:35 | 45737.8993 | 5.6334 | 0.025228 | 657 | 146711 | Unplanned | Vegetation | Forestry Block tree through line W1159 - W6359
1361 |  | N/A 83 | Kaiti, Whataupoko | Gisborne | Whangara 0506 | 2025-03-20 11:16 | 45736.4694 | 2025-03-20 12:50 | 45736.5347 | 1.1848 | 0.022616 | 589 | 30855 | Unplanned | Unknown cause | Inst O/C CB A472 - Line patrolled - No ovious cause of fault
1362 |  | 174564 | 330 Sheltons Road | Gisborne | Rototahi 0403 | 2025-03-20 16:24 | 45736.6833 | 2025-03-20 17:12 | 45736.7167 | 0.02949 | 0.00061437 | 16 | 768 | Unplanned | Unknown cause | Replace fuses
1363 |  | 30145 | Ihungia Road | Gisborne | Mata 0304 | 2025-03-21 00:51 | 45737.0354 | 2025-03-21 13:31 | 45737.5632 | 0.29371 | 0.00061437 | 16 | 7649 | Unplanned | Vegetation | Tree through HV lines at pole H650
1364 |  | N/A 84 | Thomas Rd | Gisborne | Rototahi 0403 | 2025-03-21 06:55 | 45737.2882 | 2025-03-21 08:37 | 45737.359 | 0.01175 | 0.00011519 | 3 | 306 | Unplanned | Vegetation | Tree branch on HV btwn Pole A858 - A859
1365 |  | 174195 | 63 Thomas Road | Gisborne | Rototahi 0403 | 2025-03-21 06:55 | 45737.2882 | 2025-03-21 08:55 | 45737.3715 | 0.013823 | 0.00011519 | 3 | 360 | Unplanned | Vegetation | Replace fuses
1366 |  | 174979 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-03-21 08:31 | 45737.3549 | 2025-03-21 10:30 | 45737.4375 | 0.027416 | 0.00023039 | 6 | 714 | Unplanned | Wildlife | Replace fuses
1367 |  | 175570 | 165 Glendening Road | Wairoa | Raupunga 3101 | 2025-03-22 08:56 | 45738.3722 | 2025-03-22 10:30 | 45738.4375 | 0.0072188 | 7.6796e-05 | 2 | 188 | Unplanned | Unknown cause | Replace fuse
1368 |  | 176948 | 124 Iwitea Road | Wairoa | Nuhaka 3203 | 2025-03-24 07:34 | 45740.3153 | 2025-03-24 09:10 | 45740.3819 | 0.062666 | 0.00065277 | 17 | 1632 | Unplanned | Wildlife | Replace fuses - Possible bird strike
1369 |  | 177016 | Berry Road, Tiniroto | Gisborne | Tiniroto 1003 | 2025-03-24 09:51 | 45740.4104 | 2025-03-24 12:30 | 45740.5208 | 0.085474 | 0.00053757 | 14 | 2226 | Unplanned | Unknown cause | Replace fuses
1370 |  | 3543 | Ahirau Road | Gisborne | Te Karaka 1203 | 2025-03-24 11:01 | 45740.459 | 2025-03-24 12:17 | 45740.5118 | 0.029183 | 0.00038398 | 10 | 380.1459 | Planned | Planned | Install HV fuses TX E1824 (TX not installed)
1371 |  | 177060 | 89 Walker Road | Gisborne | Ruatoria 0201 | 2025-03-24 12:21 | 45740.5146 | 2025-03-24 14:30 | 45740.6042 | 0.0049533 | 3.8398e-05 | 1 | 129 | Unplanned | Wildlife | Replace fuses
1372 |  | 3547 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-03-25 09:01 | 45741.3757 | 2025-03-25 16:04 | 45741.6694 | 0.58473 | 0.0013823 | 36 | 7624.5251 | Planned | Planned | Replace 50kV poles
1373 |  | 3565 | Tauwhareparae Rd | Gisborne | Tauwhareparae 0404 | 2025-03-25 09:02 | 45741.3764 | 2025-03-25 13:57 | 45741.5813 | 0.57678 | 0.0019583 | 51 | 7523.3153 | Planned | Planned | Install Recloser
1374 |  | 3581 | Mangahaurini Gorge | Gisborne | Inland 0301 | 2025-03-25 11:07 | 45741.4632 | 2025-03-25 13:41 | 45741.5701 | 0.0059133 | 3.8398e-05 | 1 | 154 | Planned | Planned | Urgent Shutdown - To Remove at risk tree @ pole H2408
1375 |  | 3547 A | Te Araroa Road | Gisborne | Awatere 0101 | 2025-03-25 16:30 | 45741.6875 | 2025-03-25 16:31 | 45741.6882 | 0.018162 | 0.018162 | 473 | 473 | Planned | Planned | Replace 50kV poles
1376 |  | 3546 | Wharekopare Road | Gisborne | Tahora 1103 | 2025-03-26 08:32 | 45742.3556 | 2025-03-26 16:44 | 45742.6972 | 1.0957 | 0.0022271 | 58 | 14299.7761 | Planned | Planned | Replace HV poles
1377 |  | 3548 | Bushmere Road | Gisborne | Bushmere 0805 | 2025-03-26 09:01 | 45742.3757 | 2025-03-26 14:14 | 45742.5931 | 0.55285 | 0.0017663 | 46 | 7211.7157 | Planned | Planned | Replace ABS D399
1378 |  | 3566 | Tauwhareparae Rd | Gisborne | Tauwhareparae 0404 | 2025-03-27 09:00 | 45743.375 | 2025-03-27 16:58 | 45743.7069 | 0.92282 | 0.0019583 | 51 | 11486.3437 | Planned | Planned | Install new SW/GR
1379 |  | 179128 | 35 Nicks Head Road | Gisborne | Muriwai 0905 | 2025-03-28 07:50 | 45744.3264 | 2025-03-28 09:24 | 45744.3917 | 0.0036094 | 3.8398e-05 | 1 | 94 | Unplanned | Unknown cause | Replace fuses
1380 |  | 3551 | Wharekopae Road | Gisborne | Tahora 1103 | 2025-03-28 08:30 | 45744.3542 | 2025-03-28 16:42 | 45744.6958 | 1.0957 | 0.0022271 | 58 | 14299.7761 | Planned | Planned | Replace 11kV poles
1381 |  | 3567 | Aberdeen Road | Gisborne | Gladstone 0607 | 2025-03-28 08:35 | 45744.3576 | 2025-03-28 13:08 | 45744.5472 | 1.7611 | 0.0064509 | 168 | 23079.9313 | Planned | Planned | Tree cutting
1382 |  | 3561 | Waiapu Road | Gisborne | Mata 0304 | 2025-03-28 08:44 | 45744.3639 | 2025-03-28 14:14 | 45744.5931 | 0.063357 | 0.00019199 | 5 | 825.2016 | Planned | Planned | 11kV deenergised only for 50kV pole change
1383 |  | 179169 | Kiwi Road | Wairoa | Affco 3202 | 2025-03-28 10:06 | 45744.4208 | 2025-03-28 10:40 | 45744.4444 | 0.0013055 | 3.8398e-05 | 1 | 34 | Unplanned | Unknown cause | Replace fuse
1384 |  | 179209 | 904 Poroporo Road | Gisborne | Tiki Tiki 0206 | 2025-03-28 10:52 | 45744.4528 | 2025-03-28 13:00 | 45744.5417 | 0.063894 | 0.00049917 | 13 | 1664 | Unplanned | Unknown cause | Replace fuses
1385 |  | 179241 | 211 Gordon Road | Gisborne | Te Arai 0906 | 2025-03-28 12:49 | 45744.534 | 2025-03-28 14:00 | 45744.5833 | 0.032715 | 0.00046078 | 12 | 852 | Unplanned | Unknown cause | Replace fuses
1386 |  | 30188 | Watson Park | Gisborne | Willows 0702 | 2025-03-28 12:50 | 45744.5347 | 2025-03-28 13:27 | 45744.5604 | 0.0014207 | 3.8398e-05 | 1 | 37 | Unplanned | Defective Equipment | Blown HV jumpers at TX HV Fuses B1965
1387 |  | 180613 | 416 Waiomatatini Road | Gisborne | Tiki Tiki 0206 | 2025-03-30 08:20 | 45746.3472 | 2025-03-30 09:50 | 45746.4097 | 0.0034558 | 3.8398e-05 | 1 | 90 | Unplanned | Unknown cause | Replace fuses
1388 |  | 30190 | Waimata Valley Rd / Kawatiri Road | Gisborne | Waimata 0903 | 2025-03-31 05:58 | 45747.2486 | 2025-03-31 08:41 | 45747.3618 | 1.3897 | 0.02492 | 649 | 36193 | Unplanned | Defective Equipment | Broken HV conductor between Pole D1423 - D1424. Pin loose tripped over flashover to top of pole
1389 |  | 3552 | Wharekopae Road | Gisborne | Tahora 1103 | 2025-03-31 08:30 | 45747.3542 | 2025-03-31 15:36 | 45747.65 | 0.94874 | 0.0022271 | 58 | 12381.5134 | Planned | Planned | Replace poles
1390 |  | 30199 | Paparatu Road | Gisborne | Te Arai 0906 | 2025-03-31 16:52 | 45747.7028 | 2025-03-31 20:07 | 45747.8382 | 0.10629 | 0.00061437 | 16 | 2768 | Unplanned | Defective Equipment | Burnt HV pole C863. Insulator failed, tracked thru arm
1391 |  | ¹ Extend table as necessary to disclose information for all individual interruptions
1392